## Data
| No Load | Locked rotor | Frequency (Hz) | 50
Voltage (V) | 380 | 76 | Pole | 4
Current (A) | 5.2 | 11.5 | Synchronous Speed (ns) (rpm) | 1500
Power (W) | 445 | 783
Friction Loss (W) | 70
Rdc (Ω) | 1.59
Line Voltage (V) | 380
Phase Voltage (V) | 380
Connection Types: "star" or "delta"
Connection Type | delta
Current Multiplier | 0.57735
Voltage Multiplier | 1
| No Load | Locked rotor
Phase Voltage (V) | 380 | 76
Phase Current (A) | 3.0022 | 6.6395
Phase Power (W) | 148.3333 | 261

## TEST
TEST

## Parameters
PARAMETERS FROM TEST RESULTS
1.5kW/ 4 pole | Z | 11.4466
| R1 | 2.385
| X1 | 4.8982
| R2 | 3.5356
| X2 | 4.8982
| Ym | 0.0079006
| Rc | 1155.2
| Xm | 127.3396

## Calculated Parameters
Stattor parameters
Rotor parameters

## Speed_torque
Speed (rpm) | Slip | Current^2 (I'2)2 | Current (I'2) (A) | Torque (Nm) | Input Current (A) | Power (kW)
0 | 1 | 1102.0833 | 33.1976 | 74.4183 | 33.8868 | 0
1 | 0.99933 | 1101.8484 | 33.1941 | 74.452 | 33.883 | 0.0077966
2 | 0.99867 | 1101.6132 | 33.1906 | 74.4858 | 33.8792 | 0.0156
3 | 0.998 | 1101.3777 | 33.187 | 74.5197 | 33.8754 | 0.023411
4 | 0.99733 | 1101.1418 | 33.1835 | 74.5535 | 33.8716 | 0.031229
5 | 0.99667 | 1100.9057 | 33.1799 | 74.5874 | 33.8677 | 0.039054
6 | 0.996 | 1100.6692 | 33.1763 | 74.6213 | 33.8639 | 0.046886
7 | 0.99533 | 1100.4325 | 33.1728 | 74.6552 | 33.8601 | 0.054725
8 | 0.99467 | 1100.1954 | 33.1692 | 74.6891 | 33.8562 | 0.062571
9 | 0.994 | 1099.958 | 33.1656 | 74.7231 | 33.8524 | 0.070425
10 | 0.99333 | 1099.7203 | 33.162 | 74.7571 | 33.8485 | 0.078285
11 | 0.99267 | 1099.4823 | 33.1584 | 74.7911 | 33.8447 | 0.086153
12 | 0.992 | 1099.244 | 33.1548 | 74.8251 | 33.8408 | 0.094028 | you can do this at every 50 rpm
13 | 0.99133 | 1099.0053 | 33.1512 | 74.8592 | 33.8369 | 0.10191
14 | 0.99067 | 1098.7664 | 33.1476 | 74.8933 | 33.8331 | 0.1098
15 | 0.99 | 1098.5271 | 33.144 | 74.9274 | 33.8292 | 0.1177
16 | 0.98933 | 1098.2875 | 33.1404 | 74.9615 | 33.8253 | 0.1256
17 | 0.98867 | 1098.0476 | 33.1368 | 74.9957 | 33.8214 | 0.13351
18 | 0.988 | 1097.8074 | 33.1332 | 75.0299 | 33.8175 | 0.14143
19 | 0.98733 | 1097.5669 | 33.1295 | 75.0641 | 33.8136 | 0.14935
20 | 0.98667 | 1097.326 | 33.1259 | 75.0983 | 33.8097 | 0.15729
21 | 0.986 | 1097.0849 | 33.1223 | 75.1326 | 33.8058 | 0.16523
22 | 0.98533 | 1096.8434 | 33.1186 | 75.1669 | 33.8018 | 0.17317
23 | 0.98467 | 1096.6016 | 33.115 | 75.2012 | 33.7979 | 0.18113
24 | 0.984 | 1096.3595 | 33.1113 | 75.2355 | 33.794 | 0.18909
25 | 0.98333 | 1096.117 | 33.1077 | 75.2699 | 33.79 | 0.19706
26 | 0.98267 | 1095.8743 | 33.104 | 75.3043 | 33.7861 | 0.20503
27 | 0.982 | 1095.6312 | 33.1003 | 75.3387 | 33.7821 | 0.21302
28 | 0.98133 | 1095.3878 | 33.0966 | 75.3731 | 33.7782 | 0.22101
29 | 0.98067 | 1095.1441 | 33.093 | 75.4076 | 33.7742 | 0.229
30 | 0.98 | 1094.9 | 33.0893 | 75.4421 | 33.7702 | 0.23701
31 | 0.97933 | 1094.6557 | 33.0856 | 75.4766 | 33.7662 | 0.24502
32 | 0.97867 | 1094.411 | 33.0819 | 75.5111 | 33.7622 | 0.25304
33 | 0.978 | 1094.166 | 33.0782 | 75.5456 | 33.7583 | 0.26107
34 | 0.97733 | 1093.9206 | 33.0745 | 75.5802 | 33.7543 | 0.2691
35 | 0.97667 | 1093.6749 | 33.0708 | 75.6148 | 33.7503 | 0.27714
36 | 0.976 | 1093.429 | 33.067 | 75.6495 | 33.7462 | 0.28519
37 | 0.97533 | 1093.1826 | 33.0633 | 75.6841 | 33.7422 | 0.29325
38 | 0.97467 | 1092.936 | 33.0596 | 75.7188 | 33.7382 | 0.30131
39 | 0.974 | 1092.689 | 33.0558 | 75.7535 | 33.7342 | 0.30938
40 | 0.97333 | 1092.4417 | 33.0521 | 75.7882 | 33.7301 | 0.31746
41 | 0.97267 | 1092.1941 | 33.0484 | 75.823 | 33.7261 | 0.32555
42 | 0.972 | 1091.9461 | 33.0446 | 75.8578 | 33.722 | 0.33364
43 | 0.97133 | 1091.6978 | 33.0409 | 75.8926 | 33.718 | 0.34174
44 | 0.97067 | 1091.4492 | 33.0371 | 75.9274 | 33.7139 | 0.34985
45 | 0.97 | 1091.2002 | 33.0333 | 75.9622 | 33.7099 | 0.35796
46 | 0.96933 | 1090.9509 | 33.0295 | 75.9971 | 33.7058 | 0.36609
47 | 0.96867 | 1090.7013 | 33.0258 | 76.032 | 33.7017 | 0.37422
48 | 0.968 | 1090.4514 | 33.022 | 76.067 | 33.6976 | 0.38235
49 | 0.96733 | 1090.2011 | 33.0182 | 76.1019 | 33.6935 | 0.3905
50 | 0.96667 | 1089.9504 | 33.0144 | 76.1369 | 33.6894 | 0.39865
51 | 0.966 | 1089.6995 | 33.0106 | 76.1719 | 33.6853 | 0.40681
52 | 0.96533 | 1089.4482 | 33.0068 | 76.2069 | 33.6812 | 0.41498
53 | 0.96467 | 1089.1966 | 33.003 | 76.242 | 33.6771 | 0.42315
54 | 0.964 | 1088.9446 | 32.9992 | 76.277 | 33.673 | 0.43134
55 | 0.96333 | 1088.6923 | 32.9953 | 76.3121 | 33.6688 | 0.43953
56 | 0.96267 | 1088.4396 | 32.9915 | 76.3473 | 33.6647 | 0.44772
57 | 0.962 | 1088.1866 | 32.9877 | 76.3824 | 33.6606 | 0.45593
58 | 0.96133 | 1087.9333 | 32.9838 | 76.4176 | 33.6564 | 0.46414
59 | 0.96067 | 1087.6797 | 32.98 | 76.4528 | 33.6523 | 0.47236
60 | 0.96 | 1087.4257 | 32.9761 | 76.488 | 33.6481 | 0.48059
61 | 0.95933 | 1087.1713 | 32.9723 | 76.5233 | 33.6439 | 0.48882
62 | 0.95867 | 1086.9166 | 32.9684 | 76.5586 | 33.6398 | 0.49707
63 | 0.958 | 1086.6616 | 32.9646 | 76.5939 | 33.6356 | 0.50532
64 | 0.95733 | 1086.4062 | 32.9607 | 76.6292 | 33.6314 | 0.51357
65 | 0.95667 | 1086.1505 | 32.9568 | 76.6645 | 33.6272 | 0.52184
66 | 0.956 | 1085.8944 | 32.9529 | 76.6999 | 33.623 | 0.53011
67 | 0.95533 | 1085.638 | 32.949 | 76.7353 | 33.6188 | 0.53839
68 | 0.95467 | 1085.3813 | 32.9451 | 76.7707 | 33.6146 | 0.54668
69 | 0.954 | 1085.1242 | 32.9412 | 76.8062 | 33.6103 | 0.55498
70 | 0.95333 | 1084.8667 | 32.9373 | 76.8417 | 33.6061 | 0.56328
71 | 0.95267 | 1084.6089 | 32.9334 | 76.8772 | 33.6019 | 0.57159
72 | 0.952 | 1084.3508 | 32.9295 | 76.9127 | 33.5976 | 0.57991
73 | 0.95133 | 1084.0923 | 32.9256 | 76.9482 | 33.5934 | 0.58823
74 | 0.95067 | 1083.8335 | 32.9216 | 76.9838 | 33.5891 | 0.59657
75 | 0.95 | 1083.5743 | 32.9177 | 77.0194 | 33.5849 | 0.60491
76 | 0.94933 | 1083.3147 | 32.9137 | 77.055 | 33.5806 | 0.61326
77 | 0.94867 | 1083.0549 | 32.9098 | 77.0907 | 33.5763 | 0.62161
78 | 0.948 | 1082.7946 | 32.9058 | 77.1264 | 33.572 | 0.62998
79 | 0.94733 | 1082.534 | 32.9019 | 77.1621 | 33.5677 | 0.63835
80 | 0.94667 | 1082.2731 | 32.8979 | 77.1978 | 33.5635 | 0.64673
81 | 0.946 | 1082.0118 | 32.8939 | 77.2335 | 33.5592 | 0.65512
82 | 0.94533 | 1081.7501 | 32.89 | 77.2693 | 33.5548 | 0.66351
83 | 0.94467 | 1081.4881 | 32.886 | 77.3051 | 33.5505 | 0.67192
84 | 0.944 | 1081.2257 | 32.882 | 77.3409 | 33.5462 | 0.68033
85 | 0.94333 | 1080.963 | 32.878 | 77.3768 | 33.5419 | 0.68874
86 | 0.94267 | 1080.6999 | 32.874 | 77.4127 | 33.5375 | 0.69717
87 | 0.942 | 1080.4365 | 32.87 | 77.4486 | 33.5332 | 0.7056
88 | 0.94133 | 1080.1727 | 32.866 | 77.4845 | 33.5288 | 0.71405
89 | 0.94067 | 1079.9085 | 32.862 | 77.5205 | 33.5245 | 0.7225
90 | 0.94 | 1079.644 | 32.8579 | 77.5564 | 33.5201 | 0.73095
91 | 0.93933 | 1079.3791 | 32.8539 | 77.5924 | 33.5158 | 0.73942
92 | 0.93867 | 1079.1139 | 32.8499 | 77.6285 | 33.5114 | 0.74789
93 | 0.938 | 1078.8483 | 32.8458 | 77.6645 | 33.507 | 0.75637
94 | 0.93733 | 1078.5823 | 32.8418 | 77.7006 | 33.5026 | 0.76486
95 | 0.93667 | 1078.316 | 32.8377 | 77.7367 | 33.4982 | 0.77335
96 | 0.936 | 1078.0493 | 32.8337 | 77.7728 | 33.4938 | 0.78186
97 | 0.93533 | 1077.7822 | 32.8296 | 77.809 | 33.4894 | 0.79037
98 | 0.93467 | 1077.5148 | 32.8255 | 77.8452 | 33.485 | 0.79889
99 | 0.934 | 1077.247 | 32.8214 | 77.8814 | 33.4805 | 0.80742
100 | 0.93333 | 1076.9789 | 32.8174 | 77.9176 | 33.4761 | 0.81595
101 | 0.93267 | 1076.7103 | 32.8133 | 77.9538 | 33.4717 | 0.82449
102 | 0.932 | 1076.4414 | 32.8092 | 77.9901 | 33.4672 | 0.83304
103 | 0.93133 | 1076.1722 | 32.8051 | 78.0264 | 33.4628 | 0.8416
104 | 0.93067 | 1075.9026 | 32.801 | 78.0628 | 33.4583 | 0.85017
105 | 0.93 | 1075.6326 | 32.7968 | 78.0991 | 33.4538 | 0.85874
106 | 0.92933 | 1075.3622 | 32.7927 | 78.1355 | 33.4494 | 0.86733
107 | 0.92867 | 1075.0914 | 32.7886 | 78.1719 | 33.4449 | 0.87592
108 | 0.928 | 1074.8203 | 32.7845 | 78.2083 | 33.4404 | 0.88452
109 | 0.92733 | 1074.5489 | 32.7803 | 78.2448 | 33.4359 | 0.89312
110 | 0.92667 | 1074.277 | 32.7762 | 78.2813 | 33.4314 | 0.90174
111 | 0.926 | 1074.0048 | 32.772 | 78.3178 | 33.4269 | 0.91036
112 | 0.92533 | 1073.7322 | 32.7679 | 78.3543 | 33.4223 | 0.91899
113 | 0.92467 | 1073.4592 | 32.7637 | 78.3909 | 33.4178 | 0.92763
114 | 0.924 | 1073.1858 | 32.7595 | 78.4274 | 33.4133 | 0.93627
115 | 0.92333 | 1072.9121 | 32.7553 | 78.4641 | 33.4087 | 0.94492
116 | 0.92267 | 1072.638 | 32.7512 | 78.5007 | 33.4042 | 0.95359
117 | 0.922 | 1072.3635 | 32.747 | 78.5373 | 33.3996 | 0.96226
118 | 0.92133 | 1072.0886 | 32.7428 | 78.574 | 33.3951 | 0.97093
119 | 0.92067 | 1071.8134 | 32.7386 | 78.6107 | 33.3905 | 0.97962
120 | 0.92 | 1071.5377 | 32.7344 | 78.6475 | 33.3859 | 0.98831
121 | 0.91933 | 1071.2617 | 32.7301 | 78.6842 | 33.3814 | 0.99701
122 | 0.91867 | 1070.9853 | 32.7259 | 78.721 | 33.3768 | 1.0057
123 | 0.918 | 1070.7085 | 32.7217 | 78.7578 | 33.3722 | 1.0144
124 | 0.91733 | 1070.4314 | 32.7174 | 78.7947 | 33.3676 | 1.0232
125 | 0.91667 | 1070.1538 | 32.7132 | 78.8315 | 33.3629 | 1.0319
126 | 0.916 | 1069.8759 | 32.709 | 78.8684 | 33.3583 | 1.0406
127 | 0.91533 | 1069.5976 | 32.7047 | 78.9053 | 33.3537 | 1.0494
128 | 0.91467 | 1069.3189 | 32.7004 | 78.9423 | 33.3491 | 1.0582
129 | 0.914 | 1069.0398 | 32.6962 | 78.9792 | 33.3444 | 1.0669
130 | 0.91333 | 1068.7603 | 32.6919 | 79.0162 | 33.3398 | 1.0757
131 | 0.91267 | 1068.4805 | 32.6876 | 79.0532 | 33.3351 | 1.0845
132 | 0.912 | 1068.2002 | 32.6833 | 79.0902 | 33.3304 | 1.0933
133 | 0.91133 | 1067.9196 | 32.679 | 79.1273 | 33.3258 | 1.1021
134 | 0.91067 | 1067.6386 | 32.6747 | 79.1644 | 33.3211 | 1.1109
135 | 0.91 | 1067.3571 | 32.6704 | 79.2015 | 33.3164 | 1.1197
136 | 0.90933 | 1067.0753 | 32.6661 | 79.2387 | 33.3117 | 1.1285
137 | 0.90867 | 1066.7931 | 32.6618 | 79.2758 | 33.307 | 1.1373
138 | 0.908 | 1066.5105 | 32.6575 | 79.313 | 33.3023 | 1.1462
139 | 0.90733 | 1066.2275 | 32.6531 | 79.3502 | 33.2976 | 1.155
140 | 0.90667 | 1065.9441 | 32.6488 | 79.3875 | 33.2928 | 1.1639
141 | 0.906 | 1065.6604 | 32.6445 | 79.4247 | 33.2881 | 1.1727
142 | 0.90533 | 1065.3762 | 32.6401 | 79.462 | 33.2834 | 1.1816
143 | 0.90467 | 1065.0916 | 32.6357 | 79.4993 | 33.2786 | 1.1905
144 | 0.904 | 1064.8066 | 32.6314 | 79.5367 | 33.2739 | 1.1994
145 | 0.90333 | 1064.5213 | 32.627 | 79.574 | 33.2691 | 1.2083
146 | 0.90267 | 1064.2355 | 32.6226 | 79.6114 | 33.2643 | 1.2172
147 | 0.902 | 1063.9493 | 32.6182 | 79.6488 | 33.2596 | 1.2261
148 | 0.90133 | 1063.6627 | 32.6138 | 79.6863 | 33.2548 | 1.235
149 | 0.90067 | 1063.3758 | 32.6094 | 79.7238 | 33.25 | 1.2439
150 | 0.9 | 1063.0884 | 32.605 | 79.7613 | 33.2452 | 1.2529
151 | 0.89933 | 1062.8006 | 32.6006 | 79.7988 | 33.2404 | 1.2618
152 | 0.89867 | 1062.5124 | 32.5962 | 79.8363 | 33.2355 | 1.2708
153 | 0.898 | 1062.2238 | 32.5918 | 79.8739 | 33.2307 | 1.2797
154 | 0.89733 | 1061.9348 | 32.5873 | 79.9115 | 33.2259 | 1.2887
155 | 0.89667 | 1061.6454 | 32.5829 | 79.9491 | 33.221 | 1.2977
156 | 0.896 | 1061.3556 | 32.5785 | 79.9867 | 33.2162 | 1.3067
157 | 0.89533 | 1061.0654 | 32.574 | 80.0244 | 33.2113 | 1.3157
158 | 0.89467 | 1060.7748 | 32.5695 | 80.0621 | 33.2065 | 1.3247
159 | 0.894 | 1060.4838 | 32.5651 | 80.0998 | 33.2016 | 1.3337
160 | 0.89333 | 1060.1923 | 32.5606 | 80.1376 | 33.1967 | 1.3427
161 | 0.89267 | 1059.9005 | 32.5561 | 80.1754 | 33.1918 | 1.3517
162 | 0.892 | 1059.6082 | 32.5516 | 80.2131 | 33.1869 | 1.3608
163 | 0.89133 | 1059.3155 | 32.5471 | 80.251 | 33.182 | 1.3698
164 | 0.89067 | 1059.0225 | 32.5426 | 80.2888 | 33.1771 | 1.3789
165 | 0.89 | 1058.729 | 32.5381 | 80.3267 | 33.1722 | 1.3879
166 | 0.88933 | 1058.435 | 32.5336 | 80.3646 | 33.1673 | 1.397
167 | 0.88867 | 1058.1407 | 32.5291 | 80.4025 | 33.1623 | 1.4061
168 | 0.888 | 1057.846 | 32.5245 | 80.4405 | 33.1574 | 1.4152
169 | 0.88733 | 1057.5508 | 32.52 | 80.4784 | 33.1524 | 1.4243
170 | 0.88667 | 1057.2552 | 32.5155 | 80.5164 | 33.1475 | 1.4334
171 | 0.886 | 1056.9592 | 32.5109 | 80.5545 | 33.1425 | 1.4425
172 | 0.88533 | 1056.6628 | 32.5064 | 80.5925 | 33.1375 | 1.4516
173 | 0.88467 | 1056.366 | 32.5018 | 80.6306 | 33.1325 | 1.4607
174 | 0.884 | 1056.0687 | 32.4972 | 80.6687 | 33.1275 | 1.4699
175 | 0.88333 | 1055.771 | 32.4926 | 80.7068 | 33.1225 | 1.479
176 | 0.88267 | 1055.4729 | 32.488 | 80.745 | 33.1175 | 1.4882
177 | 0.882 | 1055.1744 | 32.4834 | 80.7831 | 33.1125 | 1.4973
178 | 0.88133 | 1054.8754 | 32.4788 | 80.8213 | 33.1075 | 1.5065
179 | 0.88067 | 1054.576 | 32.4742 | 80.8596 | 33.1024 | 1.5157
180 | 0.88 | 1054.2762 | 32.4696 | 80.8978 | 33.0974 | 1.5249
181 | 0.87933 | 1053.976 | 32.465 | 80.9361 | 33.0924 | 1.5341
182 | 0.87867 | 1053.6754 | 32.4604 | 80.9744 | 33.0873 | 1.5433
183 | 0.878 | 1053.3743 | 32.4557 | 81.0127 | 33.0822 | 1.5525
184 | 0.87733 | 1053.0728 | 32.4511 | 81.0511 | 33.0771 | 1.5617
185 | 0.87667 | 1052.7708 | 32.4464 | 81.0895 | 33.0721 | 1.571
186 | 0.876 | 1052.4684 | 32.4418 | 81.1279 | 33.067 | 1.5802
187 | 0.87533 | 1052.1656 | 32.4371 | 81.1663 | 33.0619 | 1.5894
188 | 0.87467 | 1051.8624 | 32.4324 | 81.2048 | 33.0568 | 1.5987
189 | 0.874 | 1051.5587 | 32.4277 | 81.2432 | 33.0516 | 1.608
190 | 0.87333 | 1051.2546 | 32.4231 | 81.2817 | 33.0465 | 1.6172
191 | 0.87267 | 1050.9501 | 32.4184 | 81.3203 | 33.0414 | 1.6265
192 | 0.872 | 1050.6451 | 32.4137 | 81.3588 | 33.0362 | 1.6358
193 | 0.87133 | 1050.3397 | 32.4089 | 81.3974 | 33.0311 | 1.6451
194 | 0.87067 | 1050.0339 | 32.4042 | 81.436 | 33.0259 | 1.6544
195 | 0.87 | 1049.7276 | 32.3995 | 81.4746 | 33.0208 | 1.6637
196 | 0.86933 | 1049.4208 | 32.3948 | 81.5133 | 33.0156 | 1.6731
197 | 0.86867 | 1049.1137 | 32.39 | 81.552 | 33.0104 | 1.6824
198 | 0.868 | 1048.8061 | 32.3853 | 81.5907 | 33.0052 | 1.6917
199 | 0.86733 | 1048.498 | 32.3805 | 81.6294 | 33 | 1.7011
200 | 0.86667 | 1048.1895 | 32.3758 | 81.6682 | 32.9948 | 1.7105
201 | 0.866 | 1047.8806 | 32.371 | 81.707 | 32.9896 | 1.7198
202 | 0.86533 | 1047.5712 | 32.3662 | 81.7458 | 32.9843 | 1.7292
203 | 0.86467 | 1047.2614 | 32.3614 | 81.7846 | 32.9791 | 1.7386
204 | 0.864 | 1046.9512 | 32.3566 | 81.8235 | 32.9739 | 1.748
205 | 0.86333 | 1046.6405 | 32.3518 | 81.8623 | 32.9686 | 1.7574
206 | 0.86267 | 1046.3293 | 32.347 | 81.9012 | 32.9634 | 1.7668
207 | 0.862 | 1046.0177 | 32.3422 | 81.9402 | 32.9581 | 1.7762
208 | 0.86133 | 1045.7056 | 32.3374 | 81.9791 | 32.9528 | 1.7856
209 | 0.86067 | 1045.3931 | 32.3325 | 82.0181 | 32.9475 | 1.7951
210 | 0.86 | 1045.0802 | 32.3277 | 82.0571 | 32.9422 | 1.8045
211 | 0.85933 | 1044.7668 | 32.3229 | 82.0962 | 32.9369 | 1.814
212 | 0.85867 | 1044.4529 | 32.318 | 82.1352 | 32.9316 | 1.8234
213 | 0.858 | 1044.1386 | 32.3131 | 82.1743 | 32.9263 | 1.8329
214 | 0.85733 | 1043.8238 | 32.3083 | 82.2134 | 32.9209 | 1.8424
215 | 0.85667 | 1043.5086 | 32.3034 | 82.2525 | 32.9156 | 1.8519
216 | 0.856 | 1043.1929 | 32.2985 | 82.2917 | 32.9102 | 1.8614
217 | 0.85533 | 1042.8768 | 32.2936 | 82.3309 | 32.9049 | 1.8709
218 | 0.85467 | 1042.5602 | 32.2887 | 82.3701 | 32.8995 | 1.8804
219 | 0.854 | 1042.2432 | 32.2838 | 82.4093 | 32.8941 | 1.8899
220 | 0.85333 | 1041.9256 | 32.2789 | 82.4486 | 32.8888 | 1.8995
221 | 0.85267 | 1041.6077 | 32.2739 | 82.4879 | 32.8834 | 1.909
222 | 0.852 | 1041.2892 | 32.269 | 82.5272 | 32.878 | 1.9186
223 | 0.85133 | 1040.9704 | 32.2641 | 82.5665 | 32.8725 | 1.9281
224 | 0.85067 | 1040.651 | 32.2591 | 82.6058 | 32.8671 | 1.9377
225 | 0.85 | 1040.3312 | 32.2542 | 82.6452 | 32.8617 | 1.9473
226 | 0.84933 | 1040.0109 | 32.2492 | 82.6846 | 32.8563 | 1.9569
227 | 0.84867 | 1039.6902 | 32.2442 | 82.7241 | 32.8508 | 1.9665
228 | 0.848 | 1039.3689 | 32.2392 | 82.7635 | 32.8453 | 1.9761
229 | 0.84733 | 1039.0473 | 32.2343 | 82.803 | 32.8399 | 1.9857
230 | 0.84667 | 1038.7251 | 32.2293 | 82.8425 | 32.8344 | 1.9953
231 | 0.846 | 1038.4025 | 32.2243 | 82.882 | 32.8289 | 2.0049
232 | 0.84533 | 1038.0794 | 32.2192 | 82.9216 | 32.8234 | 2.0146
233 | 0.84467 | 1037.7558 | 32.2142 | 82.9612 | 32.8179 | 2.0242
234 | 0.844 | 1037.4318 | 32.2092 | 83.0008 | 32.8124 | 2.0339
235 | 0.84333 | 1037.1073 | 32.2042 | 83.0404 | 32.8069 | 2.0436
236 | 0.84267 | 1036.7823 | 32.1991 | 83.0801 | 32.8014 | 2.0532
237 | 0.842 | 1036.4569 | 32.194 | 83.1198 | 32.7958 | 2.0629
238 | 0.84133 | 1036.1309 | 32.189 | 83.1595 | 32.7903 | 2.0726
239 | 0.84067 | 1035.8045 | 32.1839 | 83.1992 | 32.7847 | 2.0823
240 | 0.84 | 1035.4776 | 32.1788 | 83.2389 | 32.7791 | 2.092
241 | 0.83933 | 1035.1503 | 32.1738 | 83.2787 | 32.7736 | 2.1017
242 | 0.83867 | 1034.8224 | 32.1687 | 83.3185 | 32.768 | 2.1115
243 | 0.838 | 1034.4941 | 32.1636 | 83.3584 | 32.7624 | 2.1212
244 | 0.83733 | 1034.1653 | 32.1584 | 83.3982 | 32.7568 | 2.131
245 | 0.83667 | 1033.836 | 32.1533 | 83.4381 | 32.7512 | 2.1407
246 | 0.836 | 1033.5063 | 32.1482 | 83.478 | 32.7455 | 2.1505
247 | 0.83533 | 1033.176 | 32.1431 | 83.5179 | 32.7399 | 2.1603
248 | 0.83467 | 1032.8453 | 32.1379 | 83.5579 | 32.7343 | 2.17
249 | 0.834 | 1032.514 | 32.1328 | 83.5978 | 32.7286 | 2.1798
250 | 0.83333 | 1032.1823 | 32.1276 | 83.6378 | 32.7229 | 2.1896
251 | 0.83267 | 1031.8501 | 32.1224 | 83.6779 | 32.7173 | 2.1994
252 | 0.832 | 1031.5175 | 32.1172 | 83.7179 | 32.7116 | 2.2093
253 | 0.83133 | 1031.1843 | 32.1121 | 83.758 | 32.7059 | 2.2191
254 | 0.83067 | 1030.8506 | 32.1069 | 83.7981 | 32.7002 | 2.2289
255 | 0.83 | 1030.5165 | 32.1017 | 83.8382 | 32.6945 | 2.2388
256 | 0.82933 | 1030.1818 | 32.0964 | 83.8783 | 32.6888 | 2.2486
257 | 0.82867 | 1029.8467 | 32.0912 | 83.9185 | 32.683 | 2.2585
258 | 0.828 | 1029.511 | 32.086 | 83.9587 | 32.6773 | 2.2684
259 | 0.82733 | 1029.1749 | 32.0808 | 83.9989 | 32.6716 | 2.2783
260 | 0.82667 | 1028.8383 | 32.0755 | 84.0392 | 32.6658 | 2.2881
261 | 0.826 | 1028.5012 | 32.0703 | 84.0794 | 32.66 | 2.298
262 | 0.82533 | 1028.1635 | 32.065 | 84.1197 | 32.6542 | 2.308
263 | 0.82467 | 1027.8254 | 32.0597 | 84.1601 | 32.6485 | 2.3179
264 | 0.824 | 1027.4868 | 32.0544 | 84.2004 | 32.6427 | 2.3278
265 | 0.82333 | 1027.1477 | 32.0491 | 84.2408 | 32.6369 | 2.3377
266 | 0.82267 | 1026.808 | 32.0438 | 84.2812 | 32.631 | 2.3477
267 | 0.822 | 1026.4679 | 32.0385 | 84.3216 | 32.6252 | 2.3576
268 | 0.82133 | 1026.1273 | 32.0332 | 84.362 | 32.6194 | 2.3676
269 | 0.82067 | 1025.7861 | 32.0279 | 84.4025 | 32.6135 | 2.3776
270 | 0.82 | 1025.4445 | 32.0226 | 84.443 | 32.6077 | 2.3876
271 | 0.81933 | 1025.1024 | 32.0172 | 84.4835 | 32.6018 | 2.3976
272 | 0.81867 | 1024.7597 | 32.0119 | 84.524 | 32.5959 | 2.4076
273 | 0.818 | 1024.4165 | 32.0065 | 84.5646 | 32.59 | 2.4176
274 | 0.81733 | 1024.0729 | 32.0011 | 84.6051 | 32.5842 | 2.4276
275 | 0.81667 | 1023.7287 | 31.9958 | 84.6457 | 32.5782 | 2.4376
276 | 0.816 | 1023.384 | 31.9904 | 84.6864 | 32.5723 | 2.4477
277 | 0.81533 | 1023.0388 | 31.985 | 84.727 | 32.5664 | 2.4577
278 | 0.81467 | 1022.693 | 31.9796 | 84.7677 | 32.5605 | 2.4678
279 | 0.814 | 1022.3468 | 31.9742 | 84.8084 | 32.5545 | 2.4778
280 | 0.81333 | 1022 | 31.9687 | 84.8491 | 32.5486 | 2.4879
281 | 0.81267 | 1021.6528 | 31.9633 | 84.8899 | 32.5426 | 2.498
282 | 0.812 | 1021.305 | 31.9579 | 84.9307 | 32.5366 | 2.5081
283 | 0.81133 | 1020.9567 | 31.9524 | 84.9715 | 32.5306 | 2.5182
284 | 0.81067 | 1020.6078 | 31.947 | 85.0123 | 32.5246 | 2.5283
285 | 0.81 | 1020.2585 | 31.9415 | 85.0531 | 32.5186 | 2.5384
286 | 0.80933 | 1019.9086 | 31.936 | 85.094 | 32.5126 | 2.5486
287 | 0.80867 | 1019.5582 | 31.9305 | 85.1349 | 32.5066 | 2.5587
288 | 0.808 | 1019.2073 | 31.925 | 85.1758 | 32.5006 | 2.5688
289 | 0.80733 | 1018.8559 | 31.9195 | 85.2167 | 32.4945 | 2.579
290 | 0.80667 | 1018.5039 | 31.914 | 85.2577 | 32.4885 | 2.5892
291 | 0.806 | 1018.1514 | 31.9085 | 85.2987 | 32.4824 | 2.5993
292 | 0.80533 | 1017.7984 | 31.903 | 85.3397 | 32.4763 | 2.6095
293 | 0.80467 | 1017.4448 | 31.8974 | 85.3807 | 32.4702 | 2.6197
294 | 0.804 | 1017.0907 | 31.8919 | 85.4218 | 32.4641 | 2.6299
295 | 0.80333 | 1016.7361 | 31.8863 | 85.4629 | 32.458 | 2.6401
296 | 0.80267 | 1016.381 | 31.8807 | 85.504 | 32.4519 | 2.6504
297 | 0.802 | 1016.0253 | 31.8752 | 85.5451 | 32.4458 | 2.6606
298 | 0.80133 | 1015.6691 | 31.8696 | 85.5863 | 32.4396 | 2.6708
299 | 0.80067 | 1015.3123 | 31.864 | 85.6274 | 32.4335 | 2.6811
300 | 0.8 | 1014.955 | 31.8584 | 85.6686 | 32.4273 | 2.6914
301 | 0.79933 | 1014.5972 | 31.8527 | 85.7099 | 32.4211 | 2.7016
302 | 0.79867 | 1014.2388 | 31.8471 | 85.7511 | 32.4149 | 2.7119
303 | 0.798 | 1013.8799 | 31.8415 | 85.7924 | 32.4087 | 2.7222
304 | 0.79733 | 1013.5205 | 31.8358 | 85.8337 | 32.4025 | 2.7325
305 | 0.79667 | 1013.1605 | 31.8302 | 85.875 | 32.3963 | 2.7428
306 | 0.796 | 1012.8 | 31.8245 | 85.9163 | 32.3901 | 2.7531
307 | 0.79533 | 1012.4389 | 31.8188 | 85.9577 | 32.3839 | 2.7635
308 | 0.79467 | 1012.0773 | 31.8132 | 85.9991 | 32.3776 | 2.7738
309 | 0.794 | 1011.7151 | 31.8075 | 86.0405 | 32.3714 | 2.7841
310 | 0.79333 | 1011.3524 | 31.8018 | 86.0819 | 32.3651 | 2.7945
311 | 0.79267 | 1010.9891 | 31.7961 | 86.1234 | 32.3588 | 2.8049
312 | 0.792 | 1010.6253 | 31.7903 | 86.1648 | 32.3525 | 2.8152
313 | 0.79133 | 1010.261 | 31.7846 | 86.2063 | 32.3462 | 2.8256
314 | 0.79067 | 1009.896 | 31.7789 | 86.2479 | 32.3399 | 2.836
315 | 0.79 | 1009.5306 | 31.7731 | 86.2894 | 32.3336 | 2.8464
316 | 0.78933 | 1009.1646 | 31.7674 | 86.331 | 32.3273 | 2.8568
317 | 0.78867 | 1008.798 | 31.7616 | 86.3726 | 32.3209 | 2.8672
318 | 0.788 | 1008.4309 | 31.7558 | 86.4142 | 32.3146 | 2.8777
319 | 0.78733 | 1008.0632 | 31.75 | 86.4558 | 32.3082 | 2.8881
320 | 0.78667 | 1007.6949 | 31.7442 | 86.4975 | 32.3018 | 2.8986
321 | 0.786 | 1007.3261 | 31.7384 | 86.5392 | 32.2954 | 2.909
322 | 0.78533 | 1006.9568 | 31.7326 | 86.5809 | 32.289 | 2.9195
323 | 0.78467 | 1006.5869 | 31.7268 | 86.6226 | 32.2826 | 2.93
324 | 0.784 | 1006.2164 | 31.7209 | 86.6643 | 32.2762 | 2.9405
325 | 0.78333 | 1005.8453 | 31.7151 | 86.7061 | 32.2698 | 2.9509
326 | 0.78267 | 1005.4737 | 31.7092 | 86.7479 | 32.2633 | 2.9615
327 | 0.782 | 1005.1015 | 31.7033 | 86.7897 | 32.2569 | 2.972
328 | 0.78133 | 1004.7288 | 31.6975 | 86.8316 | 32.2504 | 2.9825
329 | 0.78067 | 1004.3555 | 31.6916 | 86.8734 | 32.2439 | 2.993
330 | 0.78 | 1003.9816 | 31.6857 | 86.9153 | 32.2374 | 3.0036
331 | 0.77933 | 1003.6071 | 31.6798 | 86.9572 | 32.2309 | 3.0141
332 | 0.77867 | 1003.2321 | 31.6738 | 86.9991 | 32.2244 | 3.0247
333 | 0.778 | 1002.8565 | 31.6679 | 87.0411 | 32.2179 | 3.0353
334 | 0.77733 | 1002.4803 | 31.662 | 87.0831 | 32.2114 | 3.0459
335 | 0.77667 | 1002.1036 | 31.656 | 87.1251 | 32.2048 | 3.0564
336 | 0.776 | 1001.7263 | 31.6501 | 87.1671 | 32.1983 | 3.067
337 | 0.77533 | 1001.3484 | 31.6441 | 87.2091 | 32.1917 | 3.0777
338 | 0.77467 | 1000.9699 | 31.6381 | 87.2512 | 32.1851 | 3.0883
339 | 0.774 | 1000.5908 | 31.6321 | 87.2933 | 32.1785 | 3.0989
340 | 0.77333 | 1000.2112 | 31.6261 | 87.3354 | 32.1719 | 3.1096
341 | 0.77267 | 999.831 | 31.6201 | 87.3775 | 32.1653 | 3.1202
342 | 0.772 | 999.4502 | 31.6141 | 87.4196 | 32.1587 | 3.1309
343 | 0.77133 | 999.0688 | 31.608 | 87.4618 | 32.1521 | 3.1415
344 | 0.77067 | 998.6868 | 31.602 | 87.504 | 32.1454 | 3.1522
345 | 0.77 | 998.3043 | 31.596 | 87.5462 | 32.1388 | 3.1629
346 | 0.76933 | 997.9211 | 31.5899 | 87.5884 | 32.1321 | 3.1736
347 | 0.76867 | 997.5374 | 31.5838 | 87.6307 | 32.1254 | 3.1843
348 | 0.768 | 997.1531 | 31.5777 | 87.673 | 32.1187 | 3.195
349 | 0.76733 | 996.7681 | 31.5716 | 87.7153 | 32.112 | 3.2057
350 | 0.76667 | 996.3826 | 31.5655 | 87.7576 | 32.1053 | 3.2165
351 | 0.766 | 995.9965 | 31.5594 | 87.7999 | 32.0986 | 3.2272
352 | 0.76533 | 995.6098 | 31.5533 | 87.8423 | 32.0918 | 3.238
353 | 0.76467 | 995.2226 | 31.5471 | 87.8847 | 32.0851 | 3.2488
354 | 0.764 | 994.8347 | 31.541 | 87.9271 | 32.0783 | 3.2595
355 | 0.76333 | 994.4462 | 31.5348 | 87.9695 | 32.0715 | 3.2703
356 | 0.76267 | 994.0571 | 31.5287 | 88.012 | 32.0647 | 3.2811
357 | 0.762 | 993.6674 | 31.5225 | 88.0544 | 32.0579 | 3.2919
358 | 0.76133 | 993.2771 | 31.5163 | 88.0969 | 32.0511 | 3.3027
359 | 0.76067 | 992.8862 | 31.5101 | 88.1394 | 32.0443 | 3.3135
360 | 0.76 | 992.4947 | 31.5039 | 88.182 | 32.0375 | 3.3244
361 | 0.75933 | 992.1027 | 31.4977 | 88.2245 | 32.0306 | 3.3352
362 | 0.75867 | 991.7099 | 31.4914 | 88.2671 | 32.0238 | 3.3461
363 | 0.758 | 991.3166 | 31.4852 | 88.3097 | 32.0169 | 3.3569
364 | 0.75733 | 990.9227 | 31.4789 | 88.3523 | 32.01 | 3.3678
365 | 0.75667 | 990.5282 | 31.4727 | 88.3949 | 32.0031 | 3.3787
366 | 0.756 | 990.133 | 31.4664 | 88.4376 | 31.9962 | 3.3896
367 | 0.75533 | 989.7373 | 31.4601 | 88.4803 | 31.9893 | 3.4005
368 | 0.75467 | 989.3409 | 31.4538 | 88.523 | 31.9824 | 3.4114
369 | 0.754 | 988.9439 | 31.4475 | 88.5657 | 31.9754 | 3.4223
370 | 0.75333 | 988.5463 | 31.4412 | 88.6084 | 31.9685 | 3.4332
371 | 0.75267 | 988.1481 | 31.4348 | 88.6512 | 31.9615 | 3.4442
372 | 0.752 | 987.7493 | 31.4285 | 88.6939 | 31.9545 | 3.4551
373 | 0.75133 | 987.3498 | 31.4221 | 88.7367 | 31.9475 | 3.4661
374 | 0.75067 | 986.9498 | 31.4158 | 88.7796 | 31.9405 | 3.4771
375 | 0.75 | 986.5491 | 31.4094 | 88.8224 | 31.9335 | 3.488
376 | 0.74933 | 986.1477 | 31.403 | 88.8653 | 31.9265 | 3.499
377 | 0.74867 | 985.7458 | 31.3966 | 88.9081 | 31.9194 | 3.51
378 | 0.748 | 985.3432 | 31.3902 | 88.951 | 31.9124 | 3.521
379 | 0.74733 | 984.94 | 31.3838 | 88.994 | 31.9053 | 3.5321
380 | 0.74667 | 984.5362 | 31.3773 | 89.0369 | 31.8982 | 3.5431
381 | 0.746 | 984.1317 | 31.3709 | 89.0799 | 31.8911 | 3.5541
382 | 0.74533 | 983.7266 | 31.3644 | 89.1228 | 31.884 | 3.5652
383 | 0.74467 | 983.3209 | 31.3579 | 89.1658 | 31.8769 | 3.5762
384 | 0.744 | 982.9145 | 31.3515 | 89.2088 | 31.8698 | 3.5873
385 | 0.74333 | 982.5076 | 31.345 | 89.2519 | 31.8626 | 3.5984
386 | 0.74267 | 982.0999 | 31.3385 | 89.2949 | 31.8555 | 3.6095
387 | 0.742 | 981.6917 | 31.332 | 89.338 | 31.8483 | 3.6206
388 | 0.74133 | 981.2828 | 31.3254 | 89.3811 | 31.8411 | 3.6317
389 | 0.74067 | 980.8732 | 31.3189 | 89.4242 | 31.834 | 3.6428
390 | 0.74 | 980.463 | 31.3123 | 89.4674 | 31.8268 | 3.6539
391 | 0.73933 | 980.0522 | 31.3058 | 89.5105 | 31.8195 | 3.665
392 | 0.73867 | 979.6407 | 31.2992 | 89.5537 | 31.8123 | 3.6762
393 | 0.738 | 979.2286 | 31.2926 | 89.5969 | 31.8051 | 3.6873
394 | 0.73733 | 978.8159 | 31.286 | 89.6401 | 31.7978 | 3.6985
395 | 0.73667 | 978.4024 | 31.2794 | 89.6833 | 31.7905 | 3.7097
396 | 0.736 | 977.9884 | 31.2728 | 89.7266 | 31.7833 | 3.7209
397 | 0.73533 | 977.5737 | 31.2662 | 89.7698 | 31.776 | 3.7321
398 | 0.73467 | 977.1583 | 31.2595 | 89.8131 | 31.7687 | 3.7433
399 | 0.734 | 976.7423 | 31.2529 | 89.8564 | 31.7613 | 3.7545
400 | 0.73333 | 976.3256 | 31.2462 | 89.8997 | 31.754 | 3.7657
401 | 0.73267 | 975.9083 | 31.2395 | 89.9431 | 31.7467 | 3.7769
402 | 0.732 | 975.4903 | 31.2328 | 89.9864 | 31.7393 | 3.7882
403 | 0.73133 | 975.0717 | 31.2261 | 90.0298 | 31.7319 | 3.7994
404 | 0.73067 | 974.6524 | 31.2194 | 90.0732 | 31.7245 | 3.8107
405 | 0.73 | 974.2324 | 31.2127 | 90.1166 | 31.7171 | 3.822
406 | 0.72933 | 973.8118 | 31.206 | 90.16 | 31.7097 | 3.8333
407 | 0.72867 | 973.3905 | 31.1992 | 90.2035 | 31.7023 | 3.8446
408 | 0.728 | 972.9686 | 31.1924 | 90.2469 | 31.6949 | 3.8559
409 | 0.72733 | 972.5459 | 31.1857 | 90.2904 | 31.6874 | 3.8672
410 | 0.72667 | 972.1227 | 31.1789 | 90.3339 | 31.6799 | 3.8785
411 | 0.726 | 971.6987 | 31.1721 | 90.3775 | 31.6725 | 3.8898
412 | 0.72533 | 971.2741 | 31.1653 | 90.421 | 31.665 | 3.9012
413 | 0.72467 | 970.8488 | 31.1584 | 90.4645 | 31.6575 | 3.9125
414 | 0.724 | 970.4228 | 31.1516 | 90.5081 | 31.65 | 3.9239
415 | 0.72333 | 969.9962 | 31.1448 | 90.5517 | 31.6424 | 3.9353
416 | 0.72267 | 969.5688 | 31.1379 | 90.5953 | 31.6349 | 3.9466
417 | 0.722 | 969.1409 | 31.131 | 90.6389 | 31.6273 | 3.958
418 | 0.72133 | 968.7122 | 31.1241 | 90.6826 | 31.6198 | 3.9694
419 | 0.72067 | 968.2828 | 31.1172 | 90.7262 | 31.6122 | 3.9808
420 | 0.72 | 967.8528 | 31.1103 | 90.7699 | 31.6046 | 3.9923
421 | 0.71933 | 967.4221 | 31.1034 | 90.8136 | 31.597 | 4.0037
422 | 0.71867 | 966.9907 | 31.0965 | 90.8573 | 31.5893 | 4.0151
423 | 0.718 | 966.5586 | 31.0895 | 90.901 | 31.5817 | 4.0266
424 | 0.71733 | 966.1258 | 31.0826 | 90.9448 | 31.574 | 4.0381
425 | 0.71667 | 965.6924 | 31.0756 | 90.9885 | 31.5664 | 4.0495
426 | 0.716 | 965.2582 | 31.0686 | 91.0323 | 31.5587 | 4.061
427 | 0.71533 | 964.8234 | 31.0616 | 91.0761 | 31.551 | 4.0725
428 | 0.71467 | 964.3878 | 31.0546 | 91.1199 | 31.5433 | 4.084
429 | 0.714 | 963.9516 | 31.0476 | 91.1637 | 31.5356 | 4.0955
430 | 0.71333 | 963.5147 | 31.0405 | 91.2076 | 31.5278 | 4.107
431 | 0.71267 | 963.0771 | 31.0335 | 91.2514 | 31.5201 | 4.1186
432 | 0.712 | 962.6387 | 31.0264 | 91.2953 | 31.5123 | 4.1301
433 | 0.71133 | 962.1997 | 31.0193 | 91.3392 | 31.5045 | 4.1417
434 | 0.71067 | 961.76 | 31.0123 | 91.3831 | 31.4968 | 4.1532
435 | 0.71 | 961.3196 | 31.0052 | 91.427 | 31.4889 | 4.1648
436 | 0.70933 | 960.8785 | 30.998 | 91.471 | 31.4811 | 4.1764
437 | 0.70867 | 960.4367 | 30.9909 | 91.5149 | 31.4733 | 4.188
438 | 0.708 | 959.9941 | 30.9838 | 91.5589 | 31.4654 | 4.1996
439 | 0.70733 | 959.5509 | 30.9766 | 91.6029 | 31.4576 | 4.2112
440 | 0.70667 | 959.1069 | 30.9695 | 91.6468 | 31.4497 | 4.2228
441 | 0.706 | 958.6623 | 30.9623 | 91.6909 | 31.4418 | 4.2344
442 | 0.70533 | 958.2169 | 30.9551 | 91.7349 | 31.4339 | 4.2461
443 | 0.70467 | 957.7708 | 30.9479 | 91.7789 | 31.426 | 4.2577
444 | 0.704 | 957.324 | 30.9407 | 91.823 | 31.4181 | 4.2694
445 | 0.70333 | 956.8765 | 30.9334 | 91.8671 | 31.4101 | 4.281
446 | 0.70267 | 956.4283 | 30.9262 | 91.9111 | 31.4022 | 4.2927
447 | 0.702 | 955.9793 | 30.9189 | 91.9552 | 31.3942 | 4.3044
448 | 0.70133 | 955.5297 | 30.9116 | 91.9994 | 31.3862 | 4.3161
449 | 0.70067 | 955.0793 | 30.9044 | 92.0435 | 31.3782 | 4.3278
450 | 0.7 | 954.6281 | 30.8971 | 92.0876 | 31.3702 | 4.3395
451 | 0.69933 | 954.1763 | 30.8897 | 92.1318 | 31.3621 | 4.3513
452 | 0.69867 | 953.7237 | 30.8824 | 92.176 | 31.3541 | 4.363
453 | 0.698 | 953.2704 | 30.8751 | 92.2201 | 31.346 | 4.3747
454 | 0.69733 | 952.8164 | 30.8677 | 92.2643 | 31.338 | 4.3865
455 | 0.69667 | 952.3616 | 30.8604 | 92.3086 | 31.3299 | 4.3983
456 | 0.696 | 951.9062 | 30.853 | 92.3528 | 31.3218 | 4.41
457 | 0.69533 | 951.4499 | 30.8456 | 92.397 | 31.3136 | 4.4218
458 | 0.69467 | 950.993 | 30.8382 | 92.4413 | 31.3055 | 4.4336
459 | 0.694 | 950.5353 | 30.8308 | 92.4855 | 31.2974 | 4.4454
460 | 0.69333 | 950.0768 | 30.8233 | 92.5298 | 31.2892 | 4.4573
461 | 0.69267 | 949.6177 | 30.8159 | 92.5741 | 31.281 | 4.4691
462 | 0.692 | 949.1577 | 30.8084 | 92.6184 | 31.2728 | 4.4809
463 | 0.69133 | 948.6971 | 30.8009 | 92.6627 | 31.2646 | 4.4928
464 | 0.69067 | 948.2357 | 30.7934 | 92.7071 | 31.2564 | 4.5046
465 | 0.69 | 947.7735 | 30.7859 | 92.7514 | 31.2481 | 4.5165
466 | 0.68933 | 947.3106 | 30.7784 | 92.7958 | 31.2399 | 4.5284
467 | 0.68867 | 946.847 | 30.7709 | 92.8402 | 31.2316 | 4.5403
468 | 0.688 | 946.3826 | 30.7633 | 92.8845 | 31.2233 | 4.5522
469 | 0.68733 | 945.9175 | 30.7558 | 92.9289 | 31.215 | 4.5641
470 | 0.68667 | 945.4516 | 30.7482 | 92.9733 | 31.2067 | 4.576
471 | 0.686 | 944.9849 | 30.7406 | 93.0178 | 31.1984 | 4.5879
472 | 0.68533 | 944.5175 | 30.733 | 93.0622 | 31.19 | 4.5999
473 | 0.68467 | 944.0493 | 30.7254 | 93.1066 | 31.1817 | 4.6118
474 | 0.684 | 943.5804 | 30.7178 | 93.1511 | 31.1733 | 4.6238
475 | 0.68333 | 943.1107 | 30.7101 | 93.1955 | 31.1649 | 4.6357
476 | 0.68267 | 942.6403 | 30.7024 | 93.24 | 31.1565 | 4.6477
477 | 0.682 | 942.169 | 30.6948 | 93.2845 | 31.1481 | 4.6597
478 | 0.68133 | 941.6971 | 30.6871 | 93.329 | 31.1397 | 4.6717
479 | 0.68067 | 941.2243 | 30.6794 | 93.3735 | 31.1312 | 4.6837
480 | 0.68 | 940.7508 | 30.6717 | 93.418 | 31.1227 | 4.6957
481 | 0.67933 | 940.2765 | 30.6639 | 93.4626 | 31.1143 | 4.7077
482 | 0.67867 | 939.8014 | 30.6562 | 93.5071 | 31.1058 | 4.7198
483 | 0.678 | 939.3256 | 30.6484 | 93.5517 | 31.0973 | 4.7318
484 | 0.67733 | 938.849 | 30.6406 | 93.5962 | 31.0887 | 4.7439
485 | 0.67667 | 938.3716 | 30.6329 | 93.6408 | 31.0802 | 4.7559
486 | 0.676 | 937.8935 | 30.625 | 93.6854 | 31.0716 | 4.768
487 | 0.67533 | 937.4145 | 30.6172 | 93.73 | 31.063 | 4.7801
488 | 0.67467 | 936.9348 | 30.6094 | 93.7746 | 31.0545 | 4.7922
489 | 0.674 | 936.4543 | 30.6015 | 93.8192 | 31.0459 | 4.8043
490 | 0.67333 | 935.973 | 30.5937 | 93.8638 | 31.0372 | 4.8164
491 | 0.67267 | 935.4909 | 30.5858 | 93.9085 | 31.0286 | 4.8285
492 | 0.672 | 935.008 | 30.5779 | 93.9531 | 31.0199 | 4.8407
493 | 0.67133 | 934.5244 | 30.57 | 93.9978 | 31.0113 | 4.8528
494 | 0.67067 | 934.04 | 30.5621 | 94.0424 | 31.0026 | 4.865
495 | 0.67 | 933.5547 | 30.5541 | 94.0871 | 30.9939 | 4.8771
496 | 0.66933 | 933.0687 | 30.5462 | 94.1318 | 30.9852 | 4.8893
497 | 0.66867 | 932.5819 | 30.5382 | 94.1765 | 30.9764 | 4.9015
498 | 0.668 | 932.0942 | 30.5302 | 94.2212 | 30.9677 | 4.9137
499 | 0.66733 | 931.6058 | 30.5222 | 94.2659 | 30.9589 | 4.9259
500 | 0.66667 | 931.1166 | 30.5142 | 94.3106 | 30.9501 | 4.9381
501 | 0.666 | 930.6266 | 30.5062 | 94.3553 | 30.9413 | 4.9503
502 | 0.66533 | 930.1357 | 30.4981 | 94.4 | 30.9325 | 4.9625
503 | 0.66467 | 929.6441 | 30.4901 | 94.4448 | 30.9237 | 4.9748
504 | 0.664 | 929.1517 | 30.482 | 94.4895 | 30.9148 | 4.987
505 | 0.66333 | 928.6584 | 30.4739 | 94.5343 | 30.906 | 4.9993
506 | 0.66267 | 928.1644 | 30.4658 | 94.579 | 30.8971 | 5.0116
507 | 0.662 | 927.6695 | 30.4577 | 94.6238 | 30.8882 | 5.0239
508 | 0.66133 | 927.1738 | 30.4495 | 94.6686 | 30.8793 | 5.0361
509 | 0.66067 | 926.6773 | 30.4414 | 94.7134 | 30.8704 | 5.0484
510 | 0.66 | 926.18 | 30.4332 | 94.7581 | 30.8614 | 5.0608
511 | 0.65933 | 925.6818 | 30.425 | 94.8029 | 30.8525 | 5.0731
512 | 0.65867 | 925.1829 | 30.4168 | 94.8477 | 30.8435 | 5.0854
513 | 0.658 | 924.6831 | 30.4086 | 94.8926 | 30.8345 | 5.0977
514 | 0.65733 | 924.1825 | 30.4004 | 94.9374 | 30.8255 | 5.1101
515 | 0.65667 | 923.6811 | 30.3921 | 94.9822 | 30.8165 | 5.1225
516 | 0.656 | 923.1788 | 30.3839 | 95.027 | 30.8074 | 5.1348
517 | 0.65533 | 922.6758 | 30.3756 | 95.0719 | 30.7983 | 5.1472
518 | 0.65467 | 922.1718 | 30.3673 | 95.1167 | 30.7893 | 5.1596
519 | 0.654 | 921.6671 | 30.359 | 95.1615 | 30.7802 | 5.172
520 | 0.65333 | 921.1615 | 30.3506 | 95.2064 | 30.7711 | 5.1844
521 | 0.65267 | 920.6551 | 30.3423 | 95.2512 | 30.7619 | 5.1968
522 | 0.652 | 920.1479 | 30.3339 | 95.2961 | 30.7528 | 5.2092
523 | 0.65133 | 919.6398 | 30.3256 | 95.341 | 30.7436 | 5.2217
524 | 0.65067 | 919.1309 | 30.3172 | 95.3858 | 30.7345 | 5.2341
525 | 0.65 | 918.6211 | 30.3088 | 95.4307 | 30.7253 | 5.2466
526 | 0.64933 | 918.1105 | 30.3003 | 95.4756 | 30.716 | 5.259
527 | 0.64867 | 917.599 | 30.2919 | 95.5205 | 30.7068 | 5.2715
528 | 0.648 | 917.0867 | 30.2834 | 95.5654 | 30.6976 | 5.284
529 | 0.64733 | 916.5736 | 30.275 | 95.6103 | 30.6883 | 5.2965
530 | 0.64667 | 916.0596 | 30.2665 | 95.6551 | 30.679 | 5.309
531 | 0.646 | 915.5447 | 30.258 | 95.7 | 30.6697 | 5.3215
532 | 0.64533 | 915.029 | 30.2494 | 95.7449 | 30.6604 | 5.334
533 | 0.64467 | 914.5124 | 30.2409 | 95.7899 | 30.6511 | 5.3466
534 | 0.644 | 913.995 | 30.2324 | 95.8348 | 30.6417 | 5.3591
535 | 0.64333 | 913.4767 | 30.2238 | 95.8797 | 30.6324 | 5.3717
536 | 0.64267 | 912.9576 | 30.2152 | 95.9246 | 30.623 | 5.3842
537 | 0.642 | 912.4376 | 30.2066 | 95.9695 | 30.6136 | 5.3968
538 | 0.64133 | 911.9167 | 30.198 | 96.0144 | 30.6042 | 5.4094
539 | 0.64067 | 911.395 | 30.1893 | 96.0593 | 30.5947 | 5.422
540 | 0.64 | 910.8724 | 30.1807 | 96.1043 | 30.5853 | 5.4346
541 | 0.63933 | 910.3489 | 30.172 | 96.1492 | 30.5758 | 5.4472
542 | 0.63867 | 909.8245 | 30.1633 | 96.1941 | 30.5663 | 5.4598
543 | 0.638 | 909.2993 | 30.1546 | 96.239 | 30.5568 | 5.4724
544 | 0.63733 | 908.7732 | 30.1459 | 96.284 | 30.5473 | 5.4851
545 | 0.63667 | 908.2463 | 30.1371 | 96.3289 | 30.5377 | 5.4977
546 | 0.636 | 907.7184 | 30.1284 | 96.3738 | 30.5282 | 5.5104
547 | 0.63533 | 907.1897 | 30.1196 | 96.4188 | 30.5186 | 5.523
548 | 0.63467 | 906.6601 | 30.1108 | 96.4637 | 30.509 | 5.5357
549 | 0.634 | 906.1296 | 30.102 | 96.5086 | 30.4994 | 5.5484
550 | 0.63333 | 905.5982 | 30.0932 | 96.5536 | 30.4897 | 5.5611
551 | 0.63267 | 905.0659 | 30.0843 | 96.5985 | 30.4801 | 5.5738
552 | 0.632 | 904.5328 | 30.0755 | 96.6434 | 30.4704 | 5.5865
553 | 0.63133 | 903.9987 | 30.0666 | 96.6884 | 30.4607 | 5.5992
554 | 0.63067 | 903.4638 | 30.0577 | 96.7333 | 30.451 | 5.612
555 | 0.63 | 902.928 | 30.0488 | 96.7782 | 30.4413 | 5.6247
556 | 0.62933 | 902.3913 | 30.0398 | 96.8232 | 30.4316 | 5.6374
557 | 0.62867 | 901.8536 | 30.0309 | 96.8681 | 30.4218 | 5.6502
558 | 0.628 | 901.3151 | 30.0219 | 96.913 | 30.412 | 5.663
559 | 0.62733 | 900.7757 | 30.0129 | 96.9579 | 30.4022 | 5.6758
560 | 0.62667 | 900.2353 | 30.0039 | 97.0029 | 30.3924 | 5.6885
561 | 0.626 | 899.6941 | 29.9949 | 97.0478 | 30.3826 | 5.7013
562 | 0.62533 | 899.152 | 29.9859 | 97.0927 | 30.3727 | 5.7141
563 | 0.62467 | 898.6089 | 29.9768 | 97.1376 | 30.3629 | 5.727
564 | 0.624 | 898.0649 | 29.9677 | 97.1825 | 30.353 | 5.7398
565 | 0.62333 | 897.5201 | 29.9586 | 97.2275 | 30.3431 | 5.7526
566 | 0.62267 | 896.9743 | 29.9495 | 97.2724 | 30.3332 | 5.7655
567 | 0.622 | 896.4276 | 29.9404 | 97.3173 | 30.3232 | 5.7783
568 | 0.62133 | 895.88 | 29.9313 | 97.3622 | 30.3132 | 5.7912
569 | 0.62067 | 895.3314 | 29.9221 | 97.4071 | 30.3033 | 5.8041
570 | 0.62 | 894.7819 | 29.9129 | 97.452 | 30.2933 | 5.8169
571 | 0.61933 | 894.2316 | 29.9037 | 97.4969 | 30.2833 | 5.8298
572 | 0.61867 | 893.6802 | 29.8945 | 97.5418 | 30.2732 | 5.8427
573 | 0.618 | 893.128 | 29.8852 | 97.5866 | 30.2632 | 5.8556
574 | 0.61733 | 892.5748 | 29.876 | 97.6315 | 30.2531 | 5.8685
575 | 0.61667 | 892.0207 | 29.8667 | 97.6764 | 30.243 | 5.8815
576 | 0.616 | 891.4657 | 29.8574 | 97.7213 | 30.2329 | 5.8944
577 | 0.61533 | 890.9097 | 29.8481 | 97.7661 | 30.2227 | 5.9074
578 | 0.61467 | 890.3528 | 29.8388 | 97.811 | 30.2126 | 5.9203
579 | 0.614 | 889.795 | 29.8294 | 97.8558 | 30.2024 | 5.9333
580 | 0.61333 | 889.2362 | 29.8201 | 97.9007 | 30.1922 | 5.9462
581 | 0.61267 | 888.6764 | 29.8107 | 97.9455 | 30.182 | 5.9592
582 | 0.612 | 888.1158 | 29.8013 | 97.9903 | 30.1718 | 5.9722
583 | 0.61133 | 887.5542 | 29.7918 | 98.0352 | 30.1616 | 5.9852
584 | 0.61067 | 886.9916 | 29.7824 | 98.08 | 30.1513 | 5.9982
585 | 0.61 | 886.4281 | 29.7729 | 98.1248 | 30.141 | 6.0112
586 | 0.60933 | 885.8636 | 29.7635 | 98.1696 | 30.1307 | 6.0243
587 | 0.60867 | 885.2982 | 29.754 | 98.2144 | 30.1204 | 6.0373
588 | 0.608 | 884.7318 | 29.7444 | 98.2592 | 30.11 | 6.0503
589 | 0.60733 | 884.1645 | 29.7349 | 98.304 | 30.0997 | 6.0634
590 | 0.60667 | 883.5962 | 29.7253 | 98.3487 | 30.0893 | 6.0764
591 | 0.606 | 883.0269 | 29.7158 | 98.3935 | 30.0789 | 6.0895
592 | 0.60533 | 882.4567 | 29.7062 | 98.4383 | 30.0685 | 6.1026
593 | 0.60467 | 881.8855 | 29.6966 | 98.483 | 30.058 | 6.1157
594 | 0.604 | 881.3134 | 29.6869 | 98.5277 | 30.0476 | 6.1288
595 | 0.60333 | 880.7402 | 29.6773 | 98.5725 | 30.0371 | 6.1419
596 | 0.60267 | 880.1662 | 29.6676 | 98.6172 | 30.0266 | 6.155
597 | 0.602 | 879.5911 | 29.6579 | 98.6619 | 30.016 | 6.1681
598 | 0.60133 | 879.0151 | 29.6482 | 98.7066 | 30.0055 | 6.1812
599 | 0.60067 | 878.438 | 29.6385 | 98.7513 | 29.9949 | 6.1944
600 | 0.6 | 877.86 | 29.6287 | 98.7959 | 29.9844 | 6.2075
601 | 0.59933 | 877.2811 | 29.6189 | 98.8406 | 29.9738 | 6.2207
602 | 0.59867 | 876.7011 | 29.6091 | 98.8853 | 29.9631 | 6.2339
603 | 0.598 | 876.1202 | 29.5993 | 98.9299 | 29.9525 | 6.247
604 | 0.59733 | 875.5382 | 29.5895 | 98.9745 | 29.9418 | 6.2602
605 | 0.59667 | 874.9553 | 29.5796 | 99.0192 | 29.9312 | 6.2734
606 | 0.596 | 874.3714 | 29.5698 | 99.0638 | 29.9204 | 6.2866
607 | 0.59533 | 873.7865 | 29.5599 | 99.1083 | 29.9097 | 6.2998
608 | 0.59467 | 873.2006 | 29.55 | 99.1529 | 29.899 | 6.313
609 | 0.594 | 872.6137 | 29.54 | 99.1975 | 29.8882 | 6.3263
610 | 0.59333 | 872.0258 | 29.5301 | 99.242 | 29.8774 | 6.3395
611 | 0.59267 | 871.4369 | 29.5201 | 99.2866 | 29.8666 | 6.3527
612 | 0.592 | 870.8471 | 29.5101 | 99.3311 | 29.8558 | 6.366
613 | 0.59133 | 870.2562 | 29.5001 | 99.3756 | 29.845 | 6.3792
614 | 0.59067 | 869.6643 | 29.4901 | 99.4201 | 29.8341 | 6.3925
615 | 0.59 | 869.0713 | 29.48 | 99.4646 | 29.8232 | 6.4058
616 | 0.58933 | 868.4774 | 29.4699 | 99.5091 | 29.8123 | 6.4191
617 | 0.58867 | 867.8825 | 29.4598 | 99.5535 | 29.8014 | 6.4324
618 | 0.588 | 867.2865 | 29.4497 | 99.5979 | 29.7904 | 6.4457
619 | 0.58733 | 866.6896 | 29.4396 | 99.6424 | 29.7795 | 6.459
620 | 0.58667 | 866.0916 | 29.4294 | 99.6868 | 29.7685 | 6.4723
621 | 0.586 | 865.4926 | 29.4193 | 99.7312 | 29.7574 | 6.4856
622 | 0.58533 | 864.8926 | 29.4091 | 99.7755 | 29.7464 | 6.4989
623 | 0.58467 | 864.2915 | 29.3988 | 99.8199 | 29.7354 | 6.5123
624 | 0.584 | 863.6894 | 29.3886 | 99.8642 | 29.7243 | 6.5256
625 | 0.58333 | 863.0863 | 29.3783 | 99.9085 | 29.7132 | 6.539
626 | 0.58267 | 862.4822 | 29.368 | 99.9528 | 29.7021 | 6.5524
627 | 0.582 | 861.877 | 29.3577 | 99.9971 | 29.6909 | 6.5657
628 | 0.58133 | 861.2708 | 29.3474 | 100.0414 | 29.6798 | 6.5791
629 | 0.58067 | 860.6636 | 29.3371 | 100.0856 | 29.6686 | 6.5925
630 | 0.58 | 860.0553 | 29.3267 | 100.1298 | 29.6574 | 6.6059
631 | 0.57933 | 859.446 | 29.3163 | 100.174 | 29.6462 | 6.6193
632 | 0.57867 | 858.8356 | 29.3059 | 100.2182 | 29.6349 | 6.6327
633 | 0.578 | 858.2242 | 29.2955 | 100.2624 | 29.6236 | 6.6462
634 | 0.57733 | 857.6118 | 29.285 | 100.3065 | 29.6124 | 6.6596
635 | 0.57667 | 856.9983 | 29.2745 | 100.3507 | 29.601 | 6.673
636 | 0.576 | 856.3837 | 29.264 | 100.3948 | 29.5897 | 6.6865
637 | 0.57533 | 855.7681 | 29.2535 | 100.4388 | 29.5784 | 6.6999
638 | 0.57467 | 855.1515 | 29.243 | 100.4829 | 29.567 | 6.7134
639 | 0.574 | 854.5337 | 29.2324 | 100.5269 | 29.5556 | 6.7269
640 | 0.57333 | 853.915 | 29.2218 | 100.5709 | 29.5442 | 6.7403
641 | 0.57267 | 853.2951 | 29.2112 | 100.6149 | 29.5327 | 6.7538
642 | 0.572 | 852.6742 | 29.2006 | 100.6589 | 29.5213 | 6.7673
643 | 0.57133 | 852.0523 | 29.1899 | 100.7029 | 29.5098 | 6.7808
644 | 0.57067 | 851.4292 | 29.1793 | 100.7468 | 29.4983 | 6.7943
645 | 0.57 | 850.8051 | 29.1686 | 100.7907 | 29.4867 | 6.8078
646 | 0.56933 | 850.18 | 29.1578 | 100.8345 | 29.4752 | 6.8214
647 | 0.56867 | 849.5537 | 29.1471 | 100.8784 | 29.4636 | 6.8349
648 | 0.568 | 848.9264 | 29.1363 | 100.9222 | 29.452 | 6.8484
649 | 0.56733 | 848.298 | 29.1256 | 100.966 | 29.4404 | 6.862
650 | 0.56667 | 847.6685 | 29.1147 | 101.0098 | 29.4288 | 6.8755
651 | 0.566 | 847.0379 | 29.1039 | 101.0535 | 29.4171 | 6.8891
652 | 0.56533 | 846.4063 | 29.0931 | 101.0973 | 29.4054 | 6.9026
653 | 0.56467 | 845.7736 | 29.0822 | 101.141 | 29.3937 | 6.9162
654 | 0.564 | 845.1397 | 29.0713 | 101.1846 | 29.382 | 6.9298
655 | 0.56333 | 844.5048 | 29.0604 | 101.2283 | 29.3702 | 6.9434
656 | 0.56267 | 843.8688 | 29.0494 | 101.2719 | 29.3584 | 6.957
657 | 0.562 | 843.2317 | 29.0385 | 101.3155 | 29.3466 | 6.9706
658 | 0.56133 | 842.5935 | 29.0275 | 101.359 | 29.3348 | 6.9842
659 | 0.56067 | 841.9542 | 29.0164 | 101.4025 | 29.323 | 6.9978
660 | 0.56 | 841.3138 | 29.0054 | 101.446 | 29.3111 | 7.0114
661 | 0.55933 | 840.6723 | 28.9943 | 101.4895 | 29.2992 | 7.0251
662 | 0.55867 | 840.0297 | 28.9833 | 101.5329 | 29.2873 | 7.0387
663 | 0.558 | 839.386 | 28.9722 | 101.5764 | 29.2754 | 7.0524
664 | 0.55733 | 838.7412 | 28.961 | 101.6197 | 29.2634 | 7.066
665 | 0.55667 | 838.0952 | 28.9499 | 101.6631 | 29.2514 | 7.0797
666 | 0.556 | 837.4482 | 28.9387 | 101.7064 | 29.2394 | 7.0933
667 | 0.55533 | 836.8 | 28.9275 | 101.7497 | 29.2274 | 7.107
668 | 0.55467 | 836.1507 | 28.9163 | 101.7929 | 29.2153 | 7.1207
669 | 0.554 | 835.5003 | 28.905 | 101.8361 | 29.2033 | 7.1344
670 | 0.55333 | 834.8488 | 28.8938 | 101.8793 | 29.1912 | 7.1481
671 | 0.55267 | 834.1962 | 28.8825 | 101.9225 | 29.179 | 7.1618
672 | 0.552 | 833.5424 | 28.8711 | 101.9656 | 29.1669 | 7.1755
673 | 0.55133 | 832.8875 | 28.8598 | 102.0087 | 29.1547 | 7.1892
674 | 0.55067 | 832.2314 | 28.8484 | 102.0517 | 29.1425 | 7.2029
675 | 0.55 | 831.5743 | 28.837 | 102.0948 | 29.1303 | 7.2167
676 | 0.54933 | 830.916 | 28.8256 | 102.1377 | 29.1181 | 7.2304
677 | 0.54867 | 830.2565 | 28.8142 | 102.1807 | 29.1058 | 7.2441
678 | 0.548 | 829.5959 | 28.8027 | 102.2236 | 29.0935 | 7.2579
679 | 0.54733 | 828.9342 | 28.7912 | 102.2665 | 29.0812 | 7.2716
680 | 0.54667 | 828.2713 | 28.7797 | 102.3093 | 29.0689 | 7.2854
681 | 0.546 | 827.6073 | 28.7682 | 102.3521 | 29.0565 | 7.2992
682 | 0.54533 | 826.9421 | 28.7566 | 102.3949 | 29.0441 | 7.3129
683 | 0.54467 | 826.2758 | 28.745 | 102.4376 | 29.0317 | 7.3267
684 | 0.544 | 825.6083 | 28.7334 | 102.4803 | 29.0193 | 7.3405
685 | 0.54333 | 824.9397 | 28.7218 | 102.5229 | 29.0068 | 7.3543
686 | 0.54267 | 824.2699 | 28.7101 | 102.5655 | 28.9943 | 7.3681
687 | 0.542 | 823.599 | 28.6984 | 102.6081 | 28.9818 | 7.3819
688 | 0.54133 | 822.9269 | 28.6867 | 102.6506 | 28.9693 | 7.3957
689 | 0.54067 | 822.2536 | 28.675 | 102.6931 | 28.9568 | 7.4095
690 | 0.54 | 821.5792 | 28.6632 | 102.7356 | 28.9442 | 7.4233
691 | 0.53933 | 820.9036 | 28.6514 | 102.778 | 28.9316 | 7.4372
692 | 0.53867 | 820.2268 | 28.6396 | 102.8203 | 28.919 | 7.451
693 | 0.538 | 819.5489 | 28.6278 | 102.8626 | 28.9063 | 7.4648
694 | 0.53733 | 818.8697 | 28.6159 | 102.9049 | 28.8936 | 7.4787
695 | 0.53667 | 818.1894 | 28.604 | 102.9472 | 28.8809 | 7.4925
696 | 0.536 | 817.508 | 28.5921 | 102.9893 | 28.8682 | 7.5064
697 | 0.53533 | 816.8253 | 28.5802 | 103.0315 | 28.8554 | 7.5202
698 | 0.53467 | 816.1415 | 28.5682 | 103.0736 | 28.8427 | 7.5341
699 | 0.534 | 815.4564 | 28.5562 | 103.1157 | 28.8299 | 7.548
700 | 0.53333 | 814.7702 | 28.5442 | 103.1577 | 28.817 | 7.5619
701 | 0.53267 | 814.0828 | 28.5321 | 103.1996 | 28.8042 | 7.5757
702 | 0.532 | 813.3942 | 28.5201 | 103.2416 | 28.7913 | 7.5896
703 | 0.53133 | 812.7044 | 28.508 | 103.2834 | 28.7784 | 7.6035
704 | 0.53067 | 812.0134 | 28.4958 | 103.3253 | 28.7655 | 7.6174
705 | 0.53 | 811.3212 | 28.4837 | 103.367 | 28.7525 | 7.6313
706 | 0.52933 | 810.6278 | 28.4715 | 103.4088 | 28.7396 | 7.6452
707 | 0.52867 | 809.9332 | 28.4593 | 103.4505 | 28.7266 | 7.6591
708 | 0.528 | 809.2374 | 28.4471 | 103.4921 | 28.7135 | 7.6731
709 | 0.52733 | 808.5404 | 28.4348 | 103.5337 | 28.7005 | 7.687
710 | 0.52667 | 807.8422 | 28.4226 | 103.5752 | 28.6874 | 7.7009
711 | 0.526 | 807.1428 | 28.4103 | 103.6167 | 28.6743 | 7.7149
712 | 0.52533 | 806.4421 | 28.3979 | 103.6581 | 28.6612 | 7.7288
713 | 0.52467 | 805.7402 | 28.3856 | 103.6995 | 28.648 | 7.7427
714 | 0.524 | 805.0372 | 28.3732 | 103.7408 | 28.6348 | 7.7567
715 | 0.52333 | 804.3328 | 28.3608 | 103.7821 | 28.6216 | 7.7706
716 | 0.52267 | 803.6273 | 28.3483 | 103.8233 | 28.6084 | 7.7846
717 | 0.522 | 802.9206 | 28.3359 | 103.8645 | 28.5951 | 7.7986
718 | 0.52133 | 802.2126 | 28.3234 | 103.9056 | 28.5818 | 7.8125
719 | 0.52067 | 801.5033 | 28.3108 | 103.9467 | 28.5685 | 7.8265
720 | 0.52 | 800.7929 | 28.2983 | 103.9877 | 28.5552 | 7.8405
721 | 0.51933 | 800.0812 | 28.2857 | 104.0287 | 28.5418 | 7.8545
722 | 0.51867 | 799.3683 | 28.2731 | 104.0696 | 28.5284 | 7.8685
723 | 0.518 | 798.6541 | 28.2605 | 104.1104 | 28.515 | 7.8824
724 | 0.51733 | 797.9387 | 28.2478 | 104.1512 | 28.5016 | 7.8964
725 | 0.51667 | 797.2221 | 28.2351 | 104.1919 | 28.4881 | 7.9104
726 | 0.516 | 796.5042 | 28.2224 | 104.2326 | 28.4746 | 7.9244
727 | 0.51533 | 795.785 | 28.2097 | 104.2732 | 28.4611 | 7.9384
728 | 0.51467 | 795.0646 | 28.1969 | 104.3137 | 28.4476 | 7.9525
729 | 0.514 | 794.343 | 28.1841 | 104.3542 | 28.434 | 7.9665
730 | 0.51333 | 793.6201 | 28.1713 | 104.3947 | 28.4204 | 7.9805
731 | 0.51267 | 792.8959 | 28.1584 | 104.435 | 28.4067 | 7.9945
732 | 0.512 | 792.1705 | 28.1455 | 104.4753 | 28.3931 | 8.0085
733 | 0.51133 | 791.4438 | 28.1326 | 104.5156 | 28.3794 | 8.0226
734 | 0.51067 | 790.7158 | 28.1197 | 104.5558 | 28.3657 | 8.0366
735 | 0.51 | 789.9866 | 28.1067 | 104.5959 | 28.352 | 8.0506
736 | 0.50933 | 789.2561 | 28.0937 | 104.636 | 28.3382 | 8.0647
737 | 0.50867 | 788.5243 | 28.0807 | 104.676 | 28.3244 | 8.0787
738 | 0.508 | 787.7913 | 28.0676 | 104.7159 | 28.3106 | 8.0928
739 | 0.50733 | 787.057 | 28.0545 | 104.7558 | 28.2967 | 8.1068
740 | 0.50667 | 786.3214 | 28.0414 | 104.7956 | 28.2829 | 8.1209
741 | 0.506 | 785.5845 | 28.0283 | 104.8353 | 28.269 | 8.1349
742 | 0.50533 | 784.8464 | 28.0151 | 104.875 | 28.255 | 8.149
743 | 0.50467 | 784.1069 | 28.0019 | 104.9146 | 28.2411 | 8.1631
744 | 0.504 | 783.3662 | 27.9887 | 104.9541 | 28.2271 | 8.1771
745 | 0.50333 | 782.6242 | 27.9754 | 104.9936 | 28.2131 | 8.1912
746 | 0.50267 | 781.8809 | 27.9621 | 105.033 | 28.1991 | 8.2053
747 | 0.502 | 781.1363 | 27.9488 | 105.0723 | 28.185 | 8.2193
748 | 0.50133 | 780.3904 | 27.9355 | 105.1115 | 28.1709 | 8.2334
749 | 0.50067 | 779.6432 | 27.9221 | 105.1507 | 28.1568 | 8.2475
750 | 0.5 | 778.8947 | 27.9087 | 105.1899 | 28.1426 | 8.2616
751 | 0.49933 | 778.1449 | 27.8952 | 105.2289 | 28.1285 | 8.2757
752 | 0.49867 | 777.3938 | 27.8818 | 105.2679 | 28.1142 | 8.2898
753 | 0.498 | 776.6414 | 27.8683 | 105.3068 | 28.1 | 8.3039
754 | 0.49733 | 775.8876 | 27.8548 | 105.3456 | 28.0858 | 8.318
755 | 0.49667 | 775.1326 | 27.8412 | 105.3843 | 28.0715 | 8.332
756 | 0.496 | 774.3762 | 27.8276 | 105.423 | 28.0571 | 8.3461
757 | 0.49533 | 773.6186 | 27.814 | 105.4616 | 28.0428 | 8.3602
758 | 0.49467 | 772.8596 | 27.8004 | 105.5001 | 28.0284 | 8.3743
759 | 0.494 | 772.0992 | 27.7867 | 105.5386 | 28.014 | 8.3884
760 | 0.49333 | 771.3376 | 27.773 | 105.577 | 27.9996 | 8.4026
761 | 0.49267 | 770.5746 | 27.7592 | 105.6153 | 27.9851 | 8.4167
762 | 0.492 | 769.8103 | 27.7455 | 105.6535 | 27.9706 | 8.4308
763 | 0.49133 | 769.0447 | 27.7317 | 105.6916 | 27.9561 | 8.4449
764 | 0.49067 | 768.2778 | 27.7178 | 105.7297 | 27.9416 | 8.459
765 | 0.49 | 767.5095 | 27.704 | 105.7676 | 27.927 | 8.4731
766 | 0.48933 | 766.7398 | 27.6901 | 105.8055 | 27.9124 | 8.4872
767 | 0.48867 | 765.9689 | 27.6761 | 105.8433 | 27.8978 | 8.5013
768 | 0.488 | 765.1966 | 27.6622 | 105.8811 | 27.8831 | 8.5155
769 | 0.48733 | 764.4229 | 27.6482 | 105.9187 | 27.8684 | 8.5296
770 | 0.48667 | 763.6479 | 27.6342 | 105.9563 | 27.8537 | 8.5437
771 | 0.486 | 762.8715 | 27.6201 | 105.9937 | 27.8389 | 8.5578
772 | 0.48533 | 762.0938 | 27.606 | 106.0311 | 27.8242 | 8.5719
773 | 0.48467 | 761.3148 | 27.5919 | 106.0684 | 27.8093 | 8.5861
774 | 0.484 | 760.5343 | 27.5778 | 106.1057 | 27.7945 | 8.6002
775 | 0.48333 | 759.7526 | 27.5636 | 106.1428 | 27.7796 | 8.6143
776 | 0.48267 | 758.9694 | 27.5494 | 106.1798 | 27.7647 | 8.6284
777 | 0.482 | 758.1849 | 27.5352 | 106.2168 | 27.7498 | 8.6426
778 | 0.48133 | 757.3991 | 27.5209 | 106.2537 | 27.7348 | 8.6567
779 | 0.48067 | 756.6118 | 27.5066 | 106.2904 | 27.7199 | 8.6708
780 | 0.48 | 755.8232 | 27.4922 | 106.3271 | 27.7048 | 8.685
781 | 0.47933 | 755.0333 | 27.4779 | 106.3637 | 27.6898 | 8.6991
782 | 0.47867 | 754.2419 | 27.4635 | 106.4002 | 27.6747 | 8.7132
783 | 0.478 | 753.4492 | 27.449 | 106.4366 | 27.6596 | 8.7273
784 | 0.47733 | 752.6551 | 27.4346 | 106.473 | 27.6445 | 8.7415
785 | 0.47667 | 751.8596 | 27.4201 | 106.5092 | 27.6293 | 8.7556
786 | 0.476 | 751.0627 | 27.4055 | 106.5453 | 27.6141 | 8.7697
787 | 0.47533 | 750.2645 | 27.391 | 106.5813 | 27.5989 | 8.7838
788 | 0.47467 | 749.4648 | 27.3764 | 106.6173 | 27.5836 | 8.798
789 | 0.474 | 748.6638 | 27.3617 | 106.6531 | 27.5683 | 8.8121
790 | 0.47333 | 747.8614 | 27.3471 | 106.6889 | 27.553 | 8.8262
791 | 0.47267 | 747.0575 | 27.3324 | 106.7245 | 27.5377 | 8.8403
792 | 0.472 | 746.2523 | 27.3176 | 106.7601 | 27.5223 | 8.8545
793 | 0.47133 | 745.4457 | 27.3029 | 106.7955 | 27.5069 | 8.8686
794 | 0.47067 | 744.6377 | 27.2881 | 106.8308 | 27.4914 | 8.8827
795 | 0.47 | 743.8283 | 27.2732 | 106.8661 | 27.476 | 8.8968
796 | 0.46933 | 743.0174 | 27.2583 | 106.9012 | 27.4604 | 8.911
797 | 0.46867 | 742.2052 | 27.2434 | 106.9363 | 27.4449 | 8.9251
798 | 0.468 | 741.3916 | 27.2285 | 106.9712 | 27.4293 | 8.9392
799 | 0.46733 | 740.5765 | 27.2135 | 107.006 | 27.4137 | 8.9533
800 | 0.46667 | 739.76 | 27.1985 | 107.0408 | 27.3981 | 8.9674
801 | 0.466 | 738.9421 | 27.1835 | 107.0754 | 27.3825 | 8.9815
802 | 0.46533 | 738.1228 | 27.1684 | 107.1099 | 27.3668 | 8.9957
803 | 0.46467 | 737.3021 | 27.1533 | 107.1443 | 27.351 | 9.0098
804 | 0.464 | 736.4799 | 27.1382 | 107.1786 | 27.3353 | 9.0239
805 | 0.46333 | 735.6564 | 27.123 | 107.2128 | 27.3195 | 9.038
806 | 0.46267 | 734.8313 | 27.1078 | 107.2469 | 27.3037 | 9.0521
807 | 0.462 | 734.0049 | 27.0925 | 107.2808 | 27.2878 | 9.0662
808 | 0.46133 | 733.177 | 27.0772 | 107.3147 | 27.2719 | 9.0803
809 | 0.46067 | 732.3477 | 27.0619 | 107.3484 | 27.256 | 9.0944
810 | 0.46 | 731.517 | 27.0466 | 107.382 | 27.2401 | 9.1085
811 | 0.45933 | 730.6848 | 27.0312 | 107.4156 | 27.2241 | 9.1226
812 | 0.45867 | 729.8511 | 27.0158 | 107.449 | 27.2081 | 9.1366
813 | 0.458 | 729.0161 | 27.0003 | 107.4822 | 27.1921 | 9.1507
814 | 0.45733 | 728.1796 | 26.9848 | 107.5154 | 27.176 | 9.1648
815 | 0.45667 | 727.3416 | 26.9693 | 107.5485 | 27.1599 | 9.1789
816 | 0.456 | 726.5022 | 26.9537 | 107.5814 | 27.1437 | 9.193
817 | 0.45533 | 725.6613 | 26.9381 | 107.6142 | 27.1276 | 9.207
818 | 0.45467 | 724.819 | 26.9225 | 107.6469 | 27.1114 | 9.2211
819 | 0.454 | 723.9752 | 26.9068 | 107.6795 | 27.0951 | 9.2352
820 | 0.45333 | 723.1299 | 26.8911 | 107.7119 | 27.0789 | 9.2492
821 | 0.45267 | 722.2832 | 26.8753 | 107.7443 | 27.0626 | 9.2633
822 | 0.452 | 721.4351 | 26.8595 | 107.7765 | 27.0462 | 9.2774
823 | 0.45133 | 720.5854 | 26.8437 | 107.8085 | 27.0299 | 9.2914
824 | 0.45067 | 719.7343 | 26.8279 | 107.8405 | 27.0135 | 9.3055
825 | 0.45 | 718.8818 | 26.812 | 107.8723 | 26.997 | 9.3195
826 | 0.44933 | 718.0277 | 26.796 | 107.904 | 26.9806 | 9.3335
827 | 0.44867 | 717.1722 | 26.7801 | 107.9356 | 26.9641 | 9.3476
828 | 0.448 | 716.3152 | 26.7641 | 107.9671 | 26.9475 | 9.3616
829 | 0.44733 | 715.4567 | 26.748 | 107.9984 | 26.931 | 9.3756
830 | 0.44667 | 714.5968 | 26.7319 | 108.0296 | 26.9144 | 9.3896
831 | 0.446 | 713.7353 | 26.7158 | 108.0606 | 26.8977 | 9.4037
832 | 0.44533 | 712.8724 | 26.6997 | 108.0915 | 26.881 | 9.4177
833 | 0.44467 | 712.008 | 26.6835 | 108.1223 | 26.8643 | 9.4317
834 | 0.444 | 711.1421 | 26.6672 | 108.153 | 26.8476 | 9.4457
835 | 0.44333 | 710.2747 | 26.651 | 108.1835 | 26.8308 | 9.4597
836 | 0.44267 | 709.4058 | 26.6347 | 108.2139 | 26.814 | 9.4737
837 | 0.442 | 708.5354 | 26.6183 | 108.2441 | 26.7972 | 9.4876
838 | 0.44133 | 707.6636 | 26.6019 | 108.2743 | 26.7803 | 9.5016
839 | 0.44067 | 706.7902 | 26.5855 | 108.3042 | 26.7634 | 9.5156
840 | 0.44 | 705.9153 | 26.5691 | 108.3341 | 26.7465 | 9.5296
841 | 0.43933 | 705.0389 | 26.5526 | 108.3638 | 26.7295 | 9.5435
842 | 0.43867 | 704.161 | 26.536 | 108.3933 | 26.7125 | 9.5575
843 | 0.438 | 703.2816 | 26.5195 | 108.4227 | 26.6955 | 9.5714
844 | 0.43733 | 702.4007 | 26.5028 | 108.452 | 26.6784 | 9.5854
845 | 0.43667 | 701.5183 | 26.4862 | 108.4811 | 26.6613 | 9.5993
846 | 0.436 | 700.6344 | 26.4695 | 108.5101 | 26.6441 | 9.6132
847 | 0.43533 | 699.7489 | 26.4528 | 108.5389 | 26.627 | 9.6271
848 | 0.43467 | 698.8619 | 26.436 | 108.5676 | 26.6097 | 9.6411
849 | 0.434 | 697.9734 | 26.4192 | 108.5961 | 26.5925 | 9.655
850 | 0.43333 | 697.0834 | 26.4023 | 108.6245 | 26.5752 | 9.6689
851 | 0.43267 | 696.1919 | 26.3854 | 108.6527 | 26.5579 | 9.6828
852 | 0.432 | 695.2988 | 26.3685 | 108.6808 | 26.5405 | 9.6966
853 | 0.43133 | 694.4042 | 26.3516 | 108.7087 | 26.5231 | 9.7105
854 | 0.43067 | 693.5081 | 26.3345 | 108.7365 | 26.5057 | 9.7244
855 | 0.43 | 692.6104 | 26.3175 | 108.7641 | 26.4883 | 9.7382
856 | 0.42933 | 691.7112 | 26.3004 | 108.7916 | 26.4708 | 9.7521
857 | 0.42867 | 690.8105 | 26.2833 | 108.8189 | 26.4532 | 9.7659
858 | 0.428 | 689.9082 | 26.2661 | 108.846 | 26.4357 | 9.7798
859 | 0.42733 | 689.0044 | 26.2489 | 108.873 | 26.4181 | 9.7936
860 | 0.42667 | 688.0991 | 26.2316 | 108.8999 | 26.4004 | 9.8074
861 | 0.426 | 687.1922 | 26.2144 | 108.9265 | 26.3828 | 9.8212
862 | 0.42533 | 686.2837 | 26.197 | 108.953 | 26.365 | 9.835
863 | 0.42467 | 685.3737 | 26.1796 | 108.9794 | 26.3473 | 9.8488
864 | 0.424 | 684.4622 | 26.1622 | 109.0056 | 26.3295 | 9.8626
865 | 0.42333 | 683.5491 | 26.1448 | 109.0316 | 26.3117 | 9.8764
866 | 0.42267 | 682.6344 | 26.1273 | 109.0574 | 26.2938 | 9.8901
867 | 0.422 | 681.7182 | 26.1097 | 109.0831 | 26.276 | 9.9039
868 | 0.42133 | 680.8005 | 26.0922 | 109.1086 | 26.258 | 9.9176
869 | 0.42067 | 679.8811 | 26.0745 | 109.134 | 26.2401 | 9.9314
870 | 0.42 | 678.9603 | 26.0569 | 109.1592 | 26.2221 | 9.9451
871 | 0.41933 | 678.0378 | 26.0392 | 109.1842 | 26.204 | 9.9588
872 | 0.41867 | 677.1138 | 26.0214 | 109.209 | 26.186 | 9.9725
873 | 0.418 | 676.1882 | 26.0036 | 109.2336 | 26.1678 | 9.9862
874 | 0.41733 | 675.2611 | 25.9858 | 109.2581 | 26.1497 | 9.9999
875 | 0.41667 | 674.3323 | 25.9679 | 109.2824 | 26.1315 | 10.0135
876 | 0.416 | 673.402 | 25.95 | 109.3066 | 26.1133 | 10.0272
877 | 0.41533 | 672.4702 | 25.932 | 109.3305 | 26.095 | 10.0408
878 | 0.41467 | 671.5367 | 25.914 | 109.3543 | 26.0767 | 10.0545
879 | 0.414 | 670.6017 | 25.896 | 109.3779 | 26.0584 | 10.0681
880 | 0.41333 | 669.6651 | 25.8779 | 109.4013 | 26.04 | 10.0817
881 | 0.41267 | 668.7269 | 25.8598 | 109.4245 | 26.0216 | 10.0953
882 | 0.412 | 667.7871 | 25.8416 | 109.4475 | 26.0032 | 10.1089
883 | 0.41133 | 666.8458 | 25.8234 | 109.4704 | 25.9847 | 10.1225
884 | 0.41067 | 665.9028 | 25.8051 | 109.493 | 25.9662 | 10.136
885 | 0.41 | 664.9583 | 25.7868 | 109.5155 | 25.9476 | 10.1496
886 | 0.40933 | 664.0122 | 25.7684 | 109.5378 | 25.929 | 10.1631
887 | 0.40867 | 663.0645 | 25.75 | 109.5599 | 25.9104 | 10.1766
888 | 0.408 | 662.1152 | 25.7316 | 109.5818 | 25.8917 | 10.1901
889 | 0.40733 | 661.1643 | 25.7131 | 109.6035 | 25.873 | 10.2036
890 | 0.40667 | 660.2118 | 25.6946 | 109.625 | 25.8543 | 10.2171
891 | 0.406 | 659.2577 | 25.676 | 109.6464 | 25.8355 | 10.2306
892 | 0.40533 | 658.302 | 25.6574 | 109.6675 | 25.8167 | 10.244
893 | 0.40467 | 657.3447 | 25.6387 | 109.6884 | 25.7978 | 10.2575
894 | 0.404 | 656.3858 | 25.62 | 109.7092 | 25.7789 | 10.2709
895 | 0.40333 | 655.4252 | 25.6013 | 109.7297 | 25.7599 | 10.2843
896 | 0.40267 | 654.4631 | 25.5825 | 109.75 | 25.741 | 10.2977
897 | 0.402 | 653.4994 | 25.5636 | 109.7701 | 25.7219 | 10.3111
898 | 0.40133 | 652.5341 | 25.5447 | 109.7901 | 25.7029 | 10.3245
899 | 0.40067 | 651.5671 | 25.5258 | 109.8098 | 25.6838 | 10.3378
900 | 0.4 | 650.5986 | 25.5068 | 109.8293 | 25.6647 | 10.3512
901 | 0.39933 | 649.6284 | 25.4878 | 109.8486 | 25.6455 | 10.3645
902 | 0.39867 | 648.6566 | 25.4687 | 109.8677 | 25.6263 | 10.3778
903 | 0.398 | 647.6832 | 25.4496 | 109.8866 | 25.607 | 10.3911
904 | 0.39733 | 646.7081 | 25.4305 | 109.9052 | 25.5877 | 10.4044
905 | 0.39667 | 645.7315 | 25.4112 | 109.9237 | 25.5684 | 10.4176
906 | 0.396 | 644.7532 | 25.392 | 109.9419 | 25.549 | 10.4309
907 | 0.39533 | 643.7733 | 25.3727 | 109.96 | 25.5296 | 10.4441
908 | 0.39467 | 642.7918 | 25.3533 | 109.9778 | 25.5102 | 10.4573
909 | 0.394 | 641.8086 | 25.3339 | 109.9954 | 25.4907 | 10.4705
910 | 0.39333 | 640.8239 | 25.3145 | 110.0128 | 25.4711 | 10.4837
911 | 0.39267 | 639.8374 | 25.295 | 110.0299 | 25.4516 | 10.4968
912 | 0.392 | 638.8494 | 25.2755 | 110.0468 | 25.432 | 10.51
913 | 0.39133 | 637.8597 | 25.2559 | 110.0635 | 25.4123 | 10.5231
914 | 0.39067 | 636.8684 | 25.2363 | 110.08 | 25.3926 | 10.5362
915 | 0.39 | 635.8755 | 25.2166 | 110.0963 | 25.3729 | 10.5493
916 | 0.38933 | 634.8809 | 25.1968 | 110.1123 | 25.3531 | 10.5623
917 | 0.38867 | 633.8847 | 25.1771 | 110.1281 | 25.3333 | 10.5754
918 | 0.388 | 632.8869 | 25.1572 | 110.1436 | 25.3135 | 10.5884
919 | 0.38733 | 631.8874 | 25.1374 | 110.159 | 25.2936 | 10.6014
920 | 0.38667 | 630.8862 | 25.1174 | 110.1741 | 25.2736 | 10.6144
921 | 0.386 | 629.8834 | 25.0975 | 110.1889 | 25.2537 | 10.6274
922 | 0.38533 | 628.879 | 25.0775 | 110.2036 | 25.2336 | 10.6403
923 | 0.38467 | 627.873 | 25.0574 | 110.218 | 25.2136 | 10.6533
924 | 0.384 | 626.8653 | 25.0373 | 110.2321 | 25.1935 | 10.6662
925 | 0.38333 | 625.8559 | 25.0171 | 110.246 | 25.1733 | 10.6791
926 | 0.38267 | 624.8449 | 24.9969 | 110.2597 | 25.1532 | 10.6919
927 | 0.382 | 623.8322 | 24.9766 | 110.2731 | 25.1329 | 10.7048
928 | 0.38133 | 622.8179 | 24.9563 | 110.2863 | 25.1127 | 10.7176
929 | 0.38067 | 621.802 | 24.936 | 110.2992 | 25.0924 | 10.7304
930 | 0.38 | 620.7843 | 24.9155 | 110.3119 | 25.072 | 10.7432
931 | 0.37933 | 619.7651 | 24.8951 | 110.3243 | 25.0516 | 10.756
932 | 0.37867 | 618.7442 | 24.8746 | 110.3365 | 25.0312 | 10.7687
933 | 0.378 | 617.7216 | 24.854 | 110.3484 | 25.0107 | 10.7814
934 | 0.37733 | 616.6973 | 24.8334 | 110.3601 | 24.9902 | 10.7941
935 | 0.37667 | 615.6715 | 24.8127 | 110.3715 | 24.9696 | 10.8068
936 | 0.376 | 614.6439 | 24.792 | 110.3827 | 24.949 | 10.8195
937 | 0.37533 | 613.6147 | 24.7712 | 110.3936 | 24.9284 | 10.8321
938 | 0.37467 | 612.5838 | 24.7504 | 110.4042 | 24.9077 | 10.8447
939 | 0.374 | 611.5513 | 24.7296 | 110.4146 | 24.887 | 10.8573
940 | 0.37333 | 610.5171 | 24.7086 | 110.4247 | 24.8662 | 10.8698
941 | 0.37267 | 609.4812 | 24.6877 | 110.4345 | 24.8454 | 10.8824
942 | 0.372 | 608.4437 | 24.6667 | 110.4441 | 24.8246 | 10.8949
943 | 0.37133 | 607.4045 | 24.6456 | 110.4534 | 24.8037 | 10.9074
944 | 0.37067 | 606.3637 | 24.6245 | 110.4625 | 24.7827 | 10.9198
945 | 0.37 | 605.3211 | 24.6033 | 110.4712 | 24.7617 | 10.9323
946 | 0.36933 | 604.2769 | 24.582 | 110.4797 | 24.7407 | 10.9447
947 | 0.36867 | 603.2311 | 24.5608 | 110.488 | 24.7196 | 10.957
948 | 0.368 | 602.1836 | 24.5394 | 110.4959 | 24.6985 | 10.9694
949 | 0.36733 | 601.1344 | 24.518 | 110.5036 | 24.6774 | 10.9817
950 | 0.36667 | 600.0835 | 24.4966 | 110.511 | 24.6562 | 10.994
951 | 0.366 | 599.0309 | 24.4751 | 110.5181 | 24.6349 | 11.0063
952 | 0.36533 | 597.9767 | 24.4536 | 110.5249 | 24.6136 | 11.0186
953 | 0.36467 | 596.9209 | 24.432 | 110.5314 | 24.5923 | 11.0308
954 | 0.364 | 595.8633 | 24.4103 | 110.5377 | 24.5709 | 11.043
955 | 0.36333 | 594.8041 | 24.3886 | 110.5436 | 24.5495 | 11.0552
956 | 0.36267 | 593.7432 | 24.3668 | 110.5493 | 24.528 | 11.0673
957 | 0.362 | 592.6806 | 24.345 | 110.5547 | 24.5065 | 11.0794
958 | 0.36133 | 591.6163 | 24.3232 | 110.5598 | 24.485 | 11.0915
959 | 0.36067 | 590.5504 | 24.3012 | 110.5646 | 24.4634 | 11.1036
960 | 0.36 | 589.4828 | 24.2793 | 110.5691 | 24.4417 | 11.1156
961 | 0.35933 | 588.4135 | 24.2572 | 110.5733 | 24.42 | 11.1276
962 | 0.35867 | 587.3426 | 24.2352 | 110.5772 | 24.3983 | 11.1396
963 | 0.358 | 586.2699 | 24.213 | 110.5808 | 24.3765 | 11.1515
964 | 0.35733 | 585.1956 | 24.1908 | 110.5841 | 24.3547 | 11.1634
965 | 0.35667 | 584.1196 | 24.1686 | 110.5871 | 24.3328 | 11.1753
966 | 0.356 | 583.042 | 24.1463 | 110.5898 | 24.3109 | 11.1872
967 | 0.35533 | 581.9626 | 24.1239 | 110.5921 | 24.2889 | 11.199
968 | 0.35467 | 580.8816 | 24.1015 | 110.5942 | 24.2669 | 11.2108
969 | 0.354 | 579.7989 | 24.079 | 110.596 | 24.2449 | 11.2226
970 | 0.35333 | 578.7145 | 24.0565 | 110.5974 | 24.2228 | 11.2343
971 | 0.35267 | 577.6285 | 24.0339 | 110.5985 | 24.2007 | 11.246
972 | 0.352 | 576.5408 | 24.0113 | 110.5993 | 24.1785 | 11.2576
973 | 0.35133 | 575.4513 | 23.9886 | 110.5998 | 24.1562 | 11.2693
974 | 0.35067 | 574.3603 | 23.9658 | 110.6 | 24.134 | 11.2809
975 | 0.35 | 573.2675 | 23.943 | 110.5998 | 24.1116 | 11.2924
976 | 0.34933 | 572.173 | 23.9201 | 110.5993 | 24.0893 | 11.304
977 | 0.34867 | 571.0769 | 23.8972 | 110.5985 | 24.0668 | 11.3155
978 | 0.348 | 569.9791 | 23.8742 | 110.5974 | 24.0444 | 11.3269
979 | 0.34733 | 568.8796 | 23.8512 | 110.5959 | 24.0219 | 11.3384
980 | 0.34667 | 567.7784 | 23.8281 | 110.5941 | 23.9993 | 11.3498
981 | 0.346 | 566.6756 | 23.8049 | 110.592 | 23.9767 | 11.3611
982 | 0.34533 | 565.5711 | 23.7817 | 110.5895 | 23.9541 | 11.3724
983 | 0.34467 | 564.4649 | 23.7585 | 110.5867 | 23.9314 | 11.3837
984 | 0.344 | 563.357 | 23.7351 | 110.5835 | 23.9086 | 11.395
985 | 0.34333 | 562.2475 | 23.7118 | 110.58 | 23.8858 | 11.4062
986 | 0.34267 | 561.1362 | 23.6883 | 110.5762 | 23.863 | 11.4174
987 | 0.342 | 560.0233 | 23.6648 | 110.572 | 23.8401 | 11.4285
988 | 0.34133 | 558.9087 | 23.6413 | 110.5675 | 23.8172 | 11.4397
989 | 0.34067 | 557.7925 | 23.6176 | 110.5626 | 23.7942 | 11.4507
990 | 0.34 | 556.6745 | 23.594 | 110.5573 | 23.7712 | 11.4618
991 | 0.33933 | 555.5549 | 23.5702 | 110.5517 | 23.7481 | 11.4728
992 | 0.33867 | 554.4337 | 23.5464 | 110.5458 | 23.725 | 11.4837
993 | 0.338 | 553.3107 | 23.5226 | 110.5395 | 23.7018 | 11.4946
994 | 0.33733 | 552.1861 | 23.4986 | 110.5328 | 23.6786 | 11.5055
995 | 0.33667 | 551.0598 | 23.4747 | 110.5258 | 23.6553 | 11.5164
996 | 0.336 | 549.9318 | 23.4506 | 110.5184 | 23.632 | 11.5272
997 | 0.33533 | 548.8021 | 23.4265 | 110.5107 | 23.6086 | 11.5379
998 | 0.33467 | 547.6708 | 23.4024 | 110.5025 | 23.5852 | 11.5487
999 | 0.334 | 546.5378 | 23.3781 | 110.494 | 23.5617 | 11.5593
1000 | 0.33333 | 545.4032 | 23.3539 | 110.4852 | 23.5382 | 11.57
1001 | 0.33267 | 544.2669 | 23.3295 | 110.4759 | 23.5147 | 11.5806
1002 | 0.332 | 543.1289 | 23.3051 | 110.4663 | 23.4911 | 11.5911
1003 | 0.33133 | 541.9892 | 23.2807 | 110.4563 | 23.4674 | 11.6017
1004 | 0.33067 | 540.8479 | 23.2561 | 110.446 | 23.4437 | 11.6121
1005 | 0.33 | 539.7049 | 23.2315 | 110.4352 | 23.4199 | 11.6226
1006 | 0.32933 | 538.5603 | 23.2069 | 110.4241 | 23.3961 | 11.633
1007 | 0.32867 | 537.4139 | 23.1822 | 110.4125 | 23.3723 | 11.6433
1008 | 0.328 | 536.266 | 23.1574 | 110.4006 | 23.3484 | 11.6536
1009 | 0.32733 | 535.1163 | 23.1326 | 110.3883 | 23.3244 | 11.6639
1010 | 0.32667 | 533.9651 | 23.1077 | 110.3756 | 23.3004 | 11.6741
1011 | 0.326 | 532.8121 | 23.0827 | 110.3625 | 23.2764 | 11.6843
1012 | 0.32533 | 531.6575 | 23.0577 | 110.349 | 23.2523 | 11.6944
1013 | 0.32467 | 530.5012 | 23.0326 | 110.3351 | 23.2281 | 11.7045
1014 | 0.324 | 529.3433 | 23.0075 | 110.3208 | 23.2039 | 11.7145
1015 | 0.32333 | 528.1838 | 22.9822 | 110.3061 | 23.1797 | 11.7245
1016 | 0.32267 | 527.0226 | 22.957 | 110.291 | 23.1553 | 11.7344
1017 | 0.322 | 525.8597 | 22.9316 | 110.2755 | 23.131 | 11.7443
1018 | 0.32133 | 524.6952 | 22.9062 | 110.2596 | 23.1066 | 11.7542
1019 | 0.32067 | 523.529 | 22.8808 | 110.2433 | 23.0821 | 11.764
1020 | 0.32 | 522.3612 | 22.8552 | 110.2265 | 23.0576 | 11.7738
1021 | 0.31933 | 521.1918 | 22.8296 | 110.2093 | 23.0331 | 11.7835
1022 | 0.31867 | 520.0207 | 22.804 | 110.1918 | 23.0085 | 11.7931
1023 | 0.318 | 518.848 | 22.7782 | 110.1737 | 22.9838 | 11.8027
1024 | 0.31733 | 517.6736 | 22.7524 | 110.1553 | 22.9591 | 11.8123
1025 | 0.31667 | 516.4976 | 22.7266 | 110.1364 | 22.9343 | 11.8218
1026 | 0.316 | 515.32 | 22.7007 | 110.1172 | 22.9095 | 11.8313
1027 | 0.31533 | 514.1407 | 22.6747 | 110.0974 | 22.8846 | 11.8407
1028 | 0.31467 | 512.9598 | 22.6486 | 110.0773 | 22.8597 | 11.85
1029 | 0.314 | 511.7773 | 22.6225 | 110.0567 | 22.8348 | 11.8593
1030 | 0.31333 | 510.5931 | 22.5963 | 110.0357 | 22.8097 | 11.8686
1031 | 0.31267 | 509.4074 | 22.5701 | 110.0142 | 22.7847 | 11.8778
1032 | 0.312 | 508.22 | 22.5437 | 109.9923 | 22.7595 | 11.887
1033 | 0.31133 | 507.031 | 22.5173 | 109.9699 | 22.7344 | 11.8961
1034 | 0.31067 | 505.8403 | 22.4909 | 109.9471 | 22.7091 | 11.9051
1035 | 0.31 | 504.6481 | 22.4644 | 109.9239 | 22.6838 | 11.9141
1036 | 0.30933 | 503.4542 | 22.4378 | 109.9002 | 22.6585 | 11.923
1037 | 0.30867 | 502.2588 | 22.4111 | 109.876 | 22.6331 | 11.9319
1038 | 0.308 | 501.0617 | 22.3844 | 109.8514 | 22.6077 | 11.9407
1039 | 0.30733 | 499.863 | 22.3576 | 109.8263 | 22.5822 | 11.9495
1040 | 0.30667 | 498.6627 | 22.3308 | 109.8008 | 22.5566 | 11.9582
1041 | 0.306 | 497.4608 | 22.3038 | 109.7748 | 22.531 | 11.9669
1042 | 0.30533 | 496.2574 | 22.2768 | 109.7483 | 22.5054 | 11.9755
1043 | 0.30467 | 495.0523 | 22.2498 | 109.7214 | 22.4797 | 11.9841
1044 | 0.304 | 493.8456 | 22.2226 | 109.694 | 22.4539 | 11.9926
1045 | 0.30333 | 492.6374 | 22.1954 | 109.6661 | 22.4281 | 12.001
1046 | 0.30267 | 491.4275 | 22.1682 | 109.6377 | 22.4022 | 12.0094
1047 | 0.302 | 490.2161 | 22.1408 | 109.6089 | 22.3763 | 12.0177
1048 | 0.30133 | 489.0031 | 22.1134 | 109.5796 | 22.3503 | 12.026
1049 | 0.30067 | 487.7885 | 22.0859 | 109.5498 | 22.3243 | 12.0342
1050 | 0.3 | 486.5724 | 22.0584 | 109.5195 | 22.2982 | 12.0423
1051 | 0.29933 | 485.3547 | 22.0308 | 109.4887 | 22.2721 | 12.0504
1052 | 0.29867 | 484.1354 | 22.0031 | 109.4574 | 22.2459 | 12.0584
1053 | 0.298 | 482.9145 | 21.9753 | 109.4256 | 22.2196 | 12.0664
1054 | 0.29733 | 481.6921 | 21.9475 | 109.3934 | 22.1933 | 12.0743
1055 | 0.29667 | 480.4681 | 21.9196 | 109.3606 | 22.167 | 12.0821
1056 | 0.296 | 479.2426 | 21.8916 | 109.3273 | 22.1406 | 12.0899
1057 | 0.29533 | 478.0155 | 21.8636 | 109.2936 | 22.1141 | 12.0976
1058 | 0.29467 | 476.7869 | 21.8355 | 109.2593 | 22.0876 | 12.1052
1059 | 0.294 | 475.5567 | 21.8073 | 109.2245 | 22.061 | 12.1128
1060 | 0.29333 | 474.325 | 21.779 | 109.1892 | 22.0344 | 12.1203
1061 | 0.29267 | 473.0918 | 21.7507 | 109.1534 | 22.0077 | 12.1278
1062 | 0.292 | 471.857 | 21.7223 | 109.1171 | 21.9809 | 12.1352
1063 | 0.29133 | 470.6207 | 21.6938 | 109.0802 | 21.9541 | 12.1425
1064 | 0.29067 | 469.3829 | 21.6652 | 109.0428 | 21.9273 | 12.1498
1065 | 0.29 | 468.1436 | 21.6366 | 109.0049 | 21.9003 | 12.1569
1066 | 0.28933 | 466.9027 | 21.6079 | 108.9665 | 21.8734 | 12.1641
1067 | 0.28867 | 465.6603 | 21.5792 | 108.9275 | 21.8464 | 12.1711
1068 | 0.288 | 464.4164 | 21.5503 | 108.888 | 21.8193 | 12.1781
1069 | 0.28733 | 463.1711 | 21.5214 | 108.848 | 21.7921 | 12.185
1070 | 0.28667 | 461.9242 | 21.4924 | 108.8074 | 21.7649 | 12.1919
1071 | 0.286 | 460.6758 | 21.4634 | 108.7663 | 21.7377 | 12.1987
1072 | 0.28533 | 459.4259 | 21.4342 | 108.7247 | 21.7104 | 12.2054
1073 | 0.28467 | 458.1746 | 21.405 | 108.6825 | 21.683 | 12.212
1074 | 0.284 | 456.9217 | 21.3757 | 108.6397 | 21.6556 | 12.2186
1075 | 0.28333 | 455.6674 | 21.3464 | 108.5964 | 21.6281 | 12.2251
1076 | 0.28267 | 454.4117 | 21.3169 | 108.5525 | 21.6006 | 12.2315
1077 | 0.282 | 453.1544 | 21.2874 | 108.5081 | 21.573 | 12.2379
1078 | 0.28133 | 451.8957 | 21.2578 | 108.4631 | 21.5453 | 12.2442
1079 | 0.28067 | 450.6355 | 21.2282 | 108.4176 | 21.5176 | 12.2504
1080 | 0.28 | 449.3739 | 21.1984 | 108.3715 | 21.4898 | 12.2565
1081 | 0.27933 | 448.1108 | 21.1686 | 108.3248 | 21.462 | 12.2626
1082 | 0.27867 | 446.8463 | 21.1387 | 108.2775 | 21.4341 | 12.2686
1083 | 0.278 | 445.5804 | 21.1088 | 108.2297 | 21.4062 | 12.2745
1084 | 0.27733 | 444.313 | 21.0787 | 108.1813 | 21.3782 | 12.2803
1085 | 0.27667 | 443.0442 | 21.0486 | 108.1323 | 21.3501 | 12.2861
1086 | 0.276 | 441.774 | 21.0184 | 108.0827 | 21.322 | 12.2918
1087 | 0.27533 | 440.5023 | 20.9881 | 108.0325 | 21.2938 | 12.2974
1088 | 0.27467 | 439.2293 | 20.9578 | 107.9818 | 21.2656 | 12.3029
1089 | 0.274 | 437.9548 | 20.9274 | 107.9304 | 21.2373 | 12.3084
1090 | 0.27333 | 436.679 | 20.8969 | 107.8785 | 21.2089 | 12.3137
1091 | 0.27267 | 435.4017 | 20.8663 | 107.8259 | 21.1805 | 12.319
1092 | 0.272 | 434.1231 | 20.8356 | 107.7728 | 21.1521 | 12.3242
1093 | 0.27133 | 432.8431 | 20.8049 | 107.719 | 21.1235 | 12.3294
1094 | 0.27067 | 431.5617 | 20.7741 | 107.6647 | 21.0949 | 12.3344
1095 | 0.27 | 430.279 | 20.7432 | 107.6097 | 21.0663 | 12.3394
1096 | 0.26933 | 428.9948 | 20.7122 | 107.5541 | 21.0376 | 12.3443
1097 | 0.26867 | 427.7094 | 20.6811 | 107.4979 | 21.0088 | 12.3491
1098 | 0.268 | 426.4225 | 20.65 | 107.4411 | 20.98 | 12.3538
1099 | 0.26733 | 425.1344 | 20.6188 | 107.3837 | 20.9511 | 12.3585
1100 | 0.26667 | 423.8449 | 20.5875 | 107.3256 | 20.9221 | 12.363
1101 | 0.266 | 422.554 | 20.5561 | 107.2669 | 20.8931 | 12.3675
1102 | 0.26533 | 421.2619 | 20.5247 | 107.2076 | 20.864 | 12.3719
1103 | 0.26467 | 419.9684 | 20.4931 | 107.1476 | 20.8349 | 12.3762
1104 | 0.264 | 418.6736 | 20.4615 | 107.087 | 20.8057 | 12.3804
1105 | 0.26333 | 417.3776 | 20.4298 | 107.0258 | 20.7765 | 12.3845
1106 | 0.26267 | 416.0802 | 20.398 | 106.9639 | 20.7471 | 12.3886
1107 | 0.262 | 414.7815 | 20.3662 | 106.9014 | 20.7178 | 12.3925
1108 | 0.26133 | 413.4816 | 20.3342 | 106.8382 | 20.6883 | 12.3964
1109 | 0.26067 | 412.1803 | 20.3022 | 106.7743 | 20.6588 | 12.4002
1110 | 0.26 | 410.8778 | 20.2701 | 106.7098 | 20.6293 | 12.4038
1111 | 0.25933 | 409.5741 | 20.2379 | 106.6447 | 20.5996 | 12.4074
1112 | 0.25867 | 408.2691 | 20.2057 | 106.5789 | 20.57 | 12.4109
1113 | 0.258 | 406.9628 | 20.1733 | 106.5124 | 20.5402 | 12.4143
1114 | 0.25733 | 405.6554 | 20.1409 | 106.4452 | 20.5104 | 12.4177
1115 | 0.25667 | 404.3466 | 20.1084 | 106.3774 | 20.4805 | 12.4209
1116 | 0.256 | 403.0367 | 20.0758 | 106.3089 | 20.4506 | 12.424
1117 | 0.25533 | 401.7256 | 20.0431 | 106.2398 | 20.4206 | 12.4271
1118 | 0.25467 | 400.4132 | 20.0103 | 106.1699 | 20.3905 | 12.43
1119 | 0.254 | 399.0997 | 19.9775 | 106.0994 | 20.3604 | 12.4329
1120 | 0.25333 | 397.7849 | 19.9445 | 106.0281 | 20.3302 | 12.4356
1121 | 0.25267 | 396.469 | 19.9115 | 105.9562 | 20.3 | 12.4383
1122 | 0.252 | 395.1519 | 19.8784 | 105.8836 | 20.2697 | 12.4409
1123 | 0.25133 | 393.8336 | 19.8452 | 105.8103 | 20.2393 | 12.4433
1124 | 0.25067 | 392.5142 | 19.812 | 105.7363 | 20.2088 | 12.4457
1125 | 0.25 | 391.1937 | 19.7786 | 105.6615 | 20.1783 | 12.448
1126 | 0.24933 | 389.872 | 19.7452 | 105.5861 | 20.1478 | 12.4501
1127 | 0.24867 | 388.5492 | 19.7117 | 105.51 | 20.1171 | 12.4522
1128 | 0.248 | 387.2252 | 19.678 | 105.4331 | 20.0864 | 12.4542
1129 | 0.24733 | 385.9002 | 19.6443 | 105.3556 | 20.0557 | 12.456
1130 | 0.24667 | 384.574 | 19.6106 | 105.2773 | 20.0249 | 12.4578
1131 | 0.246 | 383.2468 | 19.5767 | 105.1983 | 19.994 | 12.4595
1132 | 0.24533 | 381.9185 | 19.5427 | 105.1185 | 19.963 | 12.461
1133 | 0.24467 | 380.5891 | 19.5087 | 105.038 | 19.932 | 12.4625
1134 | 0.244 | 379.2586 | 19.4746 | 104.9568 | 19.9009 | 12.4639
1135 | 0.24333 | 377.9271 | 19.4403 | 104.8749 | 19.8698 | 12.4651
1136 | 0.24267 | 376.5945 | 19.406 | 104.7922 | 19.8386 | 12.4663
1137 | 0.242 | 375.2609 | 19.3717 | 104.7088 | 19.8073 | 12.4673
1138 | 0.24133 | 373.9263 | 19.3372 | 104.6246 | 19.7759 | 12.4682
1139 | 0.24067 | 372.5907 | 19.3026 | 104.5397 | 19.7445 | 12.4691
1140 | 0.24 | 371.254 | 19.268 | 104.454 | 19.7131 | 12.4698
1141 | 0.23933 | 369.9164 | 19.2332 | 104.3676 | 19.6815 | 12.4704
1142 | 0.23867 | 368.5778 | 19.1984 | 104.2804 | 19.6499 | 12.4709
1143 | 0.238 | 367.2382 | 19.1635 | 104.1924 | 19.6182 | 12.4713
1144 | 0.23733 | 365.8977 | 19.1285 | 104.1037 | 19.5865 | 12.4716
1145 | 0.23667 | 364.5562 | 19.0934 | 104.0142 | 19.5547 | 12.4717
1146 | 0.236 | 363.2137 | 19.0582 | 103.9239 | 19.5228 | 12.4718
1147 | 0.23533 | 361.8704 | 19.0229 | 103.8328 | 19.4909 | 12.4717
1148 | 0.23467 | 360.5261 | 18.9875 | 103.741 | 19.4589 | 12.4716
1149 | 0.234 | 359.1809 | 18.9521 | 103.6484 | 19.4268 | 12.4713
1150 | 0.23333 | 357.8348 | 18.9165 | 103.555 | 19.3947 | 12.4709
1151 | 0.23267 | 356.4878 | 18.8809 | 103.4608 | 19.3625 | 12.4704
1152 | 0.232 | 355.14 | 18.8452 | 103.3658 | 19.3302 | 12.4698
1153 | 0.23133 | 353.7913 | 18.8093 | 103.27 | 19.2978 | 12.469
1154 | 0.23067 | 352.4417 | 18.7734 | 103.1734 | 19.2654 | 12.4681
1155 | 0.23 | 351.0913 | 18.7374 | 103.076 | 19.233 | 12.4672
1156 | 0.22933 | 349.7401 | 18.7013 | 102.9777 | 19.2004 | 12.4661
1157 | 0.22867 | 348.3881 | 18.6652 | 102.8787 | 19.1678 | 12.4649
1158 | 0.228 | 347.0352 | 18.6289 | 102.7789 | 19.1351 | 12.4635
1159 | 0.22733 | 345.6816 | 18.5925 | 102.6782 | 19.1024 | 12.4621
1160 | 0.22667 | 344.3272 | 18.5561 | 102.5767 | 19.0696 | 12.4605
1161 | 0.226 | 342.972 | 18.5195 | 102.4744 | 19.0367 | 12.4588
1162 | 0.22533 | 341.6161 | 18.4829 | 102.3713 | 19.0037 | 12.457
1163 | 0.22467 | 340.2595 | 18.4461 | 102.2673 | 18.9707 | 12.455
1164 | 0.224 | 338.9021 | 18.4093 | 102.1625 | 18.9376 | 12.453
1165 | 0.22333 | 337.544 | 18.3724 | 102.0568 | 18.9044 | 12.4508
1166 | 0.22267 | 336.1852 | 18.3354 | 101.9503 | 18.8712 | 12.4485
1167 | 0.222 | 334.8257 | 18.2982 | 101.8429 | 18.8379 | 12.446
1168 | 0.22133 | 333.4655 | 18.261 | 101.7347 | 18.8045 | 12.4434
1169 | 0.22067 | 332.1047 | 18.2237 | 101.6257 | 18.7711 | 12.4407
1170 | 0.22 | 330.7433 | 18.1863 | 101.5158 | 18.7376 | 12.4379
1171 | 0.21933 | 329.3812 | 18.1489 | 101.405 | 18.704 | 12.435
1172 | 0.21867 | 328.0184 | 18.1113 | 101.2933 | 18.6704 | 12.4319
1173 | 0.218 | 326.6551 | 18.0736 | 101.1808 | 18.6366 | 12.4287
1174 | 0.21733 | 325.2912 | 18.0358 | 101.0674 | 18.6028 | 12.4253
1175 | 0.21667 | 323.9267 | 17.998 | 100.9531 | 18.569 | 12.4218
1176 | 0.216 | 322.5617 | 17.96 | 100.838 | 18.5351 | 12.4182
1177 | 0.21533 | 321.1961 | 17.9219 | 100.7219 | 18.501 | 12.4145
1178 | 0.21467 | 319.8299 | 17.8838 | 100.605 | 18.467 | 12.4106
1179 | 0.214 | 318.4633 | 17.8455 | 100.4872 | 18.4328 | 12.4066
1180 | 0.21333 | 317.0961 | 17.8072 | 100.3685 | 18.3986 | 12.4025
1181 | 0.21267 | 315.7285 | 17.7688 | 100.2489 | 18.3643 | 12.3982
1182 | 0.212 | 314.3604 | 17.7302 | 100.1284 | 18.33 | 12.3938
1183 | 0.21133 | 312.9918 | 17.6916 | 100.0069 | 18.2955 | 12.3892
1184 | 0.21067 | 311.6228 | 17.6528 | 99.8846 | 18.261 | 12.3845
1185 | 0.21 | 310.2534 | 17.614 | 99.7613 | 18.2265 | 12.3797
1186 | 0.20933 | 308.8835 | 17.5751 | 99.6372 | 18.1918 | 12.3747
1187 | 0.20867 | 307.5132 | 17.5361 | 99.5121 | 18.1571 | 12.3696
1188 | 0.208 | 306.1426 | 17.4969 | 99.3861 | 18.1223 | 12.3643
1189 | 0.20733 | 304.7716 | 17.4577 | 99.2591 | 18.0874 | 12.3589
1190 | 0.20667 | 303.4003 | 17.4184 | 99.1313 | 18.0525 | 12.3534
1191 | 0.206 | 302.0286 | 17.379 | 99.0025 | 18.0175 | 12.3477
1192 | 0.20533 | 300.6566 | 17.3395 | 98.8727 | 17.9824 | 12.3419
1193 | 0.20467 | 299.2843 | 17.2998 | 98.742 | 17.9472 | 12.3359
1194 | 0.204 | 297.9117 | 17.2601 | 98.6104 | 17.912 | 12.3298
1195 | 0.20333 | 296.5389 | 17.2203 | 98.4778 | 17.8767 | 12.3235
1196 | 0.20267 | 295.1658 | 17.1804 | 98.3442 | 17.8413 | 12.3171
1197 | 0.202 | 293.7925 | 17.1404 | 98.2097 | 17.8059 | 12.3105
1198 | 0.20133 | 292.419 | 17.1003 | 98.0742 | 17.7703 | 12.3038
1199 | 0.20067 | 291.0453 | 17.06 | 97.9378 | 17.7347 | 12.297
1200 | 0.2 | 289.6714 | 17.0197 | 97.8004 | 17.6991 | 12.29
1201 | 0.19933 | 288.2973 | 16.9793 | 97.662 | 17.6633 | 12.2828
1202 | 0.19867 | 286.9231 | 16.9388 | 97.5227 | 17.6275 | 12.2755
1203 | 0.198 | 285.5487 | 16.8982 | 97.3823 | 17.5916 | 12.268
1204 | 0.19733 | 284.1743 | 16.8575 | 97.241 | 17.5556 | 12.2604
1205 | 0.19667 | 282.7998 | 16.8167 | 97.0987 | 17.5196 | 12.2526
1206 | 0.196 | 281.4252 | 16.7757 | 96.9554 | 17.4835 | 12.2447
1207 | 0.19533 | 280.0505 | 16.7347 | 96.8111 | 17.4473 | 12.2366
1208 | 0.19467 | 278.6758 | 16.6936 | 96.6658 | 17.411 | 12.2284
1209 | 0.194 | 277.3011 | 16.6524 | 96.5195 | 17.3746 | 12.22
1210 | 0.19333 | 275.9264 | 16.611 | 96.3722 | 17.3382 | 12.2114
1211 | 0.19267 | 274.5518 | 16.5696 | 96.2239 | 17.3017 | 12.2027
1212 | 0.192 | 273.1771 | 16.5281 | 96.0745 | 17.2651 | 12.1938
1213 | 0.19133 | 271.8026 | 16.4864 | 95.9242 | 17.2285 | 12.1848
1214 | 0.19067 | 270.4281 | 16.4447 | 95.7728 | 17.1917 | 12.1756
1215 | 0.19 | 269.0537 | 16.4029 | 95.6204 | 17.1549 | 12.1662
1216 | 0.18933 | 267.6794 | 16.3609 | 95.4669 | 17.1181 | 12.1567
1217 | 0.18867 | 266.3053 | 16.3189 | 95.3125 | 17.0811 | 12.147
1218 | 0.188 | 264.9314 | 16.2767 | 95.157 | 17.0441 | 12.1371
1219 | 0.18733 | 263.5576 | 16.2345 | 95.0004 | 17.0069 | 12.1271
1220 | 0.18667 | 262.184 | 16.1921 | 94.8428 | 16.9697 | 12.1169
1221 | 0.186 | 260.8107 | 16.1496 | 94.6842 | 16.9325 | 12.1066
1222 | 0.18533 | 259.4375 | 16.1071 | 94.5245 | 16.8951 | 12.0961
1223 | 0.18467 | 258.0647 | 16.0644 | 94.3638 | 16.8577 | 12.0854
1224 | 0.184 | 256.6921 | 16.0216 | 94.2019 | 16.8202 | 12.0745
1225 | 0.18333 | 255.3199 | 15.9787 | 94.0391 | 16.7826 | 12.0635
1226 | 0.18267 | 253.948 | 15.9357 | 93.8751 | 16.745 | 12.0523
1227 | 0.182 | 252.5764 | 15.8927 | 93.7101 | 16.7072 | 12.0409
1228 | 0.18133 | 251.2052 | 15.8495 | 93.544 | 16.6694 | 12.0294
1229 | 0.18067 | 249.8344 | 15.8062 | 93.3769 | 16.6315 | 12.0177
1230 | 0.18 | 248.464 | 15.7627 | 93.2086 | 16.5935 | 12.0058
1231 | 0.17933 | 247.094 | 15.7192 | 93.0393 | 16.5555 | 11.9937
1232 | 0.17867 | 245.7245 | 15.6756 | 92.8689 | 16.5173 | 11.9815
1233 | 0.178 | 244.3555 | 15.6319 | 92.6973 | 16.4791 | 11.969
1234 | 0.17733 | 242.987 | 15.588 | 92.5247 | 16.4408 | 11.9564
1235 | 0.17667 | 241.619 | 15.5441 | 92.351 | 16.4025 | 11.9437
1236 | 0.176 | 240.2516 | 15.5001 | 92.1762 | 16.364 | 11.9307
1237 | 0.17533 | 238.8847 | 15.4559 | 92.0003 | 16.3255 | 11.9176
1238 | 0.17467 | 237.5185 | 15.4116 | 91.8232 | 16.2869 | 11.9042
1239 | 0.174 | 236.1528 | 15.3673 | 91.645 | 16.2482 | 11.8907
1240 | 0.17333 | 234.7878 | 15.3228 | 91.4658 | 16.2094 | 11.8771
1241 | 0.17267 | 233.4235 | 15.2782 | 91.2854 | 16.1705 | 11.8632
1242 | 0.172 | 232.0598 | 15.2335 | 91.1038 | 16.1316 | 11.8491
1243 | 0.17133 | 230.6969 | 15.1887 | 90.9212 | 16.0926 | 11.8349
1244 | 0.17067 | 229.3347 | 15.1438 | 90.7374 | 16.0535 | 11.8205
1245 | 0.17 | 227.9733 | 15.0988 | 90.5524 | 16.0143 | 11.8059
1246 | 0.16933 | 226.6127 | 15.0537 | 90.3664 | 15.9751 | 11.7911
1247 | 0.16867 | 225.2529 | 15.0084 | 90.1792 | 15.9357 | 11.7761
1248 | 0.168 | 223.8939 | 14.9631 | 89.9908 | 15.8963 | 11.7609
1249 | 0.16733 | 222.5357 | 14.9176 | 89.8013 | 15.8568 | 11.7456
1250 | 0.16667 | 221.1785 | 14.8721 | 89.6106 | 15.8172 | 11.73
1251 | 0.166 | 219.8222 | 14.8264 | 89.4187 | 15.7775 | 11.7142
1252 | 0.16533 | 218.4668 | 14.7806 | 89.2257 | 15.7378 | 11.6983
1253 | 0.16467 | 217.1124 | 14.7347 | 89.0316 | 15.6979 | 11.6822
1254 | 0.164 | 215.759 | 14.6887 | 88.8362 | 15.658 | 11.6658
1255 | 0.16333 | 214.4065 | 14.6426 | 88.6397 | 15.618 | 11.6493
1256 | 0.16267 | 213.0552 | 14.5964 | 88.442 | 15.5779 | 11.6326
1257 | 0.162 | 211.7049 | 14.5501 | 88.2431 | 15.5378 | 11.6157
1258 | 0.16133 | 210.3557 | 14.5036 | 88.0431 | 15.4975 | 11.5986
1259 | 0.16067 | 209.0076 | 14.4571 | 87.8418 | 15.4572 | 11.5813
1260 | 0.16 | 207.6606 | 14.4104 | 87.6394 | 15.4168 | 11.5637
1261 | 0.15933 | 206.3149 | 14.3637 | 87.4357 | 15.3763 | 11.546
1262 | 0.15867 | 204.9703 | 14.3168 | 87.2309 | 15.3357 | 11.5281
1263 | 0.158 | 203.627 | 14.2698 | 87.0249 | 15.295 | 11.51
1264 | 0.15733 | 202.2849 | 14.2227 | 86.8176 | 15.2543 | 11.4917
1265 | 0.15667 | 200.9441 | 14.1755 | 86.6091 | 15.2134 | 11.4732
1266 | 0.156 | 199.6046 | 14.1282 | 86.3995 | 15.1725 | 11.4544
1267 | 0.15533 | 198.2665 | 14.0807 | 86.1886 | 15.1315 | 11.4355
1268 | 0.15467 | 196.9297 | 14.0332 | 85.9765 | 15.0904 | 11.4164
1269 | 0.154 | 195.5943 | 13.9855 | 85.7631 | 15.0492 | 11.397
1270 | 0.15333 | 194.2604 | 13.9377 | 85.5486 | 15.0079 | 11.3775
1271 | 0.15267 | 192.9279 | 13.8898 | 85.3328 | 14.9666 | 11.3577
1272 | 0.152 | 191.5969 | 13.8419 | 85.1158 | 14.9252 | 11.3377
1273 | 0.15133 | 190.2674 | 13.7937 | 84.8975 | 14.8836 | 11.3175
1274 | 0.15067 | 188.9394 | 13.7455 | 84.678 | 14.842 | 11.2971
1275 | 0.15 | 187.613 | 13.6972 | 84.4572 | 14.8003 | 11.2765
1276 | 0.14933 | 186.2882 | 13.6487 | 84.2352 | 14.7586 | 11.2557
1277 | 0.14867 | 184.9651 | 13.6002 | 84.012 | 14.7167 | 11.2347
1278 | 0.148 | 183.6436 | 13.5515 | 83.7875 | 14.6747 | 11.2134
1279 | 0.14733 | 182.3238 | 13.5027 | 83.5617 | 14.6327 | 11.192
1280 | 0.14667 | 181.0057 | 13.4538 | 83.3347 | 14.5906 | 11.1703
1281 | 0.146 | 179.6893 | 13.4048 | 83.1064 | 14.5483 | 11.1484
1282 | 0.14533 | 178.3747 | 13.3557 | 82.8768 | 14.506 | 11.1263
1283 | 0.14467 | 177.062 | 13.3065 | 82.646 | 14.4637 | 11.1039
1284 | 0.144 | 175.751 | 13.2571 | 82.4139 | 14.4212 | 11.0814
1285 | 0.14333 | 174.442 | 13.2076 | 82.1805 | 14.3786 | 11.0586
1286 | 0.14267 | 173.1348 | 13.1581 | 81.9459 | 14.336 | 11.0356
1287 | 0.142 | 171.8296 | 13.1084 | 81.7099 | 14.2932 | 11.0124
1288 | 0.14133 | 170.5264 | 13.0586 | 81.4727 | 14.2504 | 10.989
1289 | 0.14067 | 169.2251 | 13.0087 | 81.2342 | 14.2075 | 10.9653
1290 | 0.14 | 167.9259 | 12.9586 | 80.9944 | 14.1645 | 10.9414
1291 | 0.13933 | 166.6287 | 12.9085 | 80.7532 | 14.1214 | 10.9173
1292 | 0.13867 | 165.3337 | 12.8582 | 80.5108 | 14.0782 | 10.8929
1293 | 0.138 | 164.0407 | 12.8078 | 80.2671 | 14.0349 | 10.8684
1294 | 0.13733 | 162.7499 | 12.7573 | 80.0221 | 13.9915 | 10.8436
1295 | 0.13667 | 161.4613 | 12.7067 | 79.7758 | 13.9481 | 10.8186
1296 | 0.136 | 160.1749 | 12.656 | 79.5281 | 13.9045 | 10.7933
1297 | 0.13533 | 158.8908 | 12.6052 | 79.2792 | 13.8609 | 10.7678
1298 | 0.13467 | 157.609 | 12.5542 | 79.0289 | 13.8172 | 10.7421
1299 | 0.134 | 156.3295 | 12.5032 | 78.7773 | 13.7733 | 10.7162
1300 | 0.13333 | 155.0523 | 12.452 | 78.5244 | 13.7294 | 10.69
1301 | 0.13267 | 153.7775 | 12.4007 | 78.2701 | 13.6854 | 10.6636
1302 | 0.132 | 152.5052 | 12.3493 | 78.0146 | 13.6414 | 10.6369
1303 | 0.13133 | 151.2353 | 12.2978 | 77.7577 | 13.5972 | 10.61
1304 | 0.13067 | 149.9678 | 12.2461 | 77.4994 | 13.5529 | 10.5829
1305 | 0.13 | 148.703 | 12.1944 | 77.2398 | 13.5085 | 10.5555
1306 | 0.12933 | 147.4406 | 12.1425 | 76.9789 | 13.4641 | 10.5279
1307 | 0.12867 | 146.1809 | 12.0905 | 76.7167 | 13.4195 | 10.5001
1308 | 0.128 | 144.9238 | 12.0384 | 76.453 | 13.3749 | 10.472
1309 | 0.12733 | 143.6693 | 11.9862 | 76.1881 | 13.3302 | 10.4437
1310 | 0.12667 | 142.4176 | 11.9339 | 75.9218 | 13.2854 | 10.4152
1311 | 0.126 | 141.1685 | 11.8814 | 75.6541 | 13.2404 | 10.3864
1312 | 0.12533 | 139.9223 | 11.8289 | 75.3851 | 13.1954 | 10.3573
1313 | 0.12467 | 138.6788 | 11.7762 | 75.1147 | 13.1503 | 10.328
1314 | 0.124 | 137.4382 | 11.7234 | 74.843 | 13.1051 | 10.2985
1315 | 0.12333 | 136.2005 | 11.6705 | 74.5698 | 13.0599 | 10.2688
1316 | 0.12267 | 134.9656 | 11.6175 | 74.2954 | 13.0145 | 10.2387
1317 | 0.122 | 133.7338 | 11.5643 | 74.0195 | 12.969 | 10.2085
1318 | 0.12133 | 132.5048 | 11.5111 | 73.7423 | 12.9234 | 10.178
1319 | 0.12067 | 131.279 | 11.4577 | 73.4637 | 12.8778 | 10.1472
1320 | 0.12 | 130.0561 | 11.4042 | 73.1837 | 12.832 | 10.1162
1321 | 0.11933 | 128.8364 | 11.3506 | 72.9024 | 12.7862 | 10.0849
1322 | 0.11867 | 127.6198 | 11.2969 | 72.6197 | 12.7402 | 10.0534
1323 | 0.118 | 126.4063 | 11.2431 | 72.3356 | 12.6942 | 10.0217
1324 | 0.11733 | 125.196 | 11.1891 | 72.0501 | 12.6481 | 9.9897
1325 | 0.11667 | 123.989 | 11.135 | 71.7632 | 12.6018 | 9.9574
1326 | 0.116 | 122.7853 | 11.0809 | 71.4749 | 12.5555 | 9.9249
1327 | 0.11533 | 121.5849 | 11.0266 | 71.1852 | 12.5091 | 9.8921
1328 | 0.11467 | 120.3878 | 10.9721 | 70.8941 | 12.4626 | 9.8591
1329 | 0.114 | 119.1941 | 10.9176 | 70.6017 | 12.416 | 9.8258
1330 | 0.11333 | 118.0038 | 10.863 | 70.3078 | 12.3693 | 9.7923
1331 | 0.11267 | 116.817 | 10.8082 | 70.0125 | 12.3225 | 9.7585
1332 | 0.112 | 115.6337 | 10.7533 | 69.7159 | 12.2756 | 9.7244
1333 | 0.11133 | 114.454 | 10.6983 | 69.4178 | 12.2286 | 9.6901
1334 | 0.11067 | 113.2778 | 10.6432 | 69.1183 | 12.1815 | 9.6556
1335 | 0.11 | 112.1052 | 10.588 | 68.8174 | 12.1343 | 9.6207
1336 | 0.10933 | 110.9363 | 10.5326 | 68.5151 | 12.087 | 9.5856
1337 | 0.10867 | 109.7711 | 10.4772 | 68.2114 | 12.0396 | 9.5503
1338 | 0.108 | 108.6097 | 10.4216 | 67.9063 | 11.9922 | 9.5147
1339 | 0.10733 | 107.452 | 10.3659 | 67.5997 | 11.9446 | 9.4788
1340 | 0.10667 | 106.2981 | 10.3101 | 67.2918 | 11.8969 | 9.4427
1341 | 0.106 | 105.1481 | 10.2542 | 66.9824 | 11.8491 | 9.4063
1342 | 0.10533 | 104.0019 | 10.1981 | 66.6716 | 11.8013 | 9.3696
1343 | 0.10467 | 102.8597 | 10.142 | 66.3593 | 11.7533 | 9.3327
1344 | 0.104 | 101.7215 | 10.0857 | 66.0457 | 11.7052 | 9.2955
1345 | 0.10333 | 100.5872 | 10.0293 | 65.7306 | 11.6571 | 9.258
1346 | 0.10267 | 99.457 | 9.9728 | 65.4141 | 11.6088 | 9.2203
1347 | 0.102 | 98.331 | 9.9162 | 65.0961 | 11.5604 | 9.1823
1348 | 0.10133 | 97.209 | 9.8595 | 64.7768 | 11.512 | 9.144
1349 | 0.10067 | 96.0912 | 9.8026 | 64.456 | 11.4634 | 9.1055
1350 | 0.1 | 94.9776 | 9.7456 | 64.1337 | 11.4148 | 9.0667
1351 | 0.099333 | 93.8683 | 9.6886 | 63.8101 | 11.366 | 9.0276
1352 | 0.098667 | 92.7633 | 9.6314 | 63.485 | 11.3171 | 8.9883
1353 | 0.098 | 91.6626 | 9.5741 | 63.1584 | 11.2682 | 8.9487
1354 | 0.097333 | 90.5663 | 9.5166 | 62.8304 | 11.2191 | 8.9088
1355 | 0.096667 | 89.4744 | 9.4591 | 62.501 | 11.17 | 8.8686
1356 | 0.096 | 88.3869 | 9.4014 | 62.1701 | 11.1207 | 8.8282
1357 | 0.095333 | 87.304 | 9.3437 | 61.8378 | 11.0713 | 8.7874
1358 | 0.094667 | 86.2256 | 9.2858 | 61.5041 | 11.0219 | 8.7465
1359 | 0.094 | 85.1517 | 9.2278 | 61.1689 | 10.9723 | 8.7052
1360 | 0.093333 | 84.0825 | 9.1697 | 60.8323 | 10.9226 | 8.6637
1361 | 0.092667 | 83.018 | 9.1114 | 60.4942 | 10.8729 | 8.6218
1362 | 0.092 | 81.9581 | 9.0531 | 60.1547 | 10.823 | 8.5798
1363 | 0.091333 | 80.903 | 8.9946 | 59.8137 | 10.773 | 8.5374
1364 | 0.090667 | 79.8527 | 8.936 | 59.4713 | 10.723 | 8.4947
1365 | 0.09 | 78.8073 | 8.8773 | 59.1274 | 10.6728 | 8.4518
1366 | 0.089333 | 77.7667 | 8.8185 | 58.7821 | 10.6225 | 8.4086
1367 | 0.088667 | 76.731 | 8.7596 | 58.4353 | 10.5721 | 8.3651
1368 | 0.088 | 75.7003 | 8.7006 | 58.0871 | 10.5217 | 8.3214
1369 | 0.087333 | 74.6746 | 8.6414 | 57.7375 | 10.4711 | 8.2773
1370 | 0.086667 | 73.6539 | 8.5822 | 57.3863 | 10.4204 | 8.233
1371 | 0.086 | 72.6383 | 8.5228 | 57.0338 | 10.3696 | 8.1884
1372 | 0.085333 | 71.6278 | 8.4633 | 56.6798 | 10.3187 | 8.1435
1373 | 0.084667 | 70.6225 | 8.4037 | 56.3243 | 10.2677 | 8.0983
1374 | 0.084 | 69.6224 | 8.344 | 55.9674 | 10.2166 | 8.0529
1375 | 0.083333 | 68.6276 | 8.2842 | 55.609 | 10.1654 | 8.0071
1376 | 0.082667 | 67.6381 | 8.2242 | 55.2492 | 10.1141 | 7.9611
1377 | 0.082 | 66.6539 | 8.1642 | 54.8879 | 10.0626 | 7.9148
1378 | 0.081333 | 65.6751 | 8.104 | 54.5252 | 10.0111 | 7.8682
1379 | 0.080667 | 64.7017 | 8.0437 | 54.161 | 9.9595 | 7.8213
1380 | 0.08 | 63.7338 | 7.9833 | 53.7954 | 9.9078 | 7.7741
1381 | 0.079333 | 62.7714 | 7.9228 | 53.4283 | 9.8559 | 7.7267
1382 | 0.078667 | 61.8146 | 7.8622 | 53.0598 | 9.804 | 7.679
1383 | 0.078 | 60.8634 | 7.8015 | 52.6898 | 9.7519 | 7.6309
1384 | 0.077333 | 59.9178 | 7.7407 | 52.3184 | 9.6998 | 7.5826
1385 | 0.076667 | 58.9779 | 7.6797 | 51.9455 | 9.6475 | 7.534
1386 | 0.076 | 58.0437 | 7.6186 | 51.5712 | 9.5952 | 7.4851
1387 | 0.075333 | 57.1153 | 7.5575 | 51.1954 | 9.5427 | 7.4359
1388 | 0.074667 | 56.1928 | 7.4962 | 50.8181 | 9.4901 | 7.3865
1389 | 0.074 | 55.2761 | 7.4348 | 50.4395 | 9.4374 | 7.3367
1390 | 0.073333 | 54.3653 | 7.3733 | 50.0593 | 9.3846 | 7.2867
1391 | 0.072667 | 53.4604 | 7.3117 | 49.6778 | 9.3317 | 7.2363
1392 | 0.072 | 52.5616 | 7.2499 | 49.2948 | 9.2787 | 7.1857
1393 | 0.071333 | 51.6687 | 7.1881 | 48.9103 | 9.2256 | 7.1348
1394 | 0.070667 | 50.782 | 7.1261 | 48.5244 | 9.1724 | 7.0836
1395 | 0.07 | 49.9014 | 7.0641 | 48.1371 | 9.119 | 7.0321
1396 | 0.069333 | 49.0269 | 7.0019 | 47.7483 | 9.0656 | 6.9803
1397 | 0.068667 | 48.1587 | 6.9396 | 47.358 | 9.012 | 6.9282
1398 | 0.068 | 47.2967 | 6.8773 | 46.9664 | 8.9584 | 6.8758
1399 | 0.067333 | 46.441 | 6.8148 | 46.5733 | 8.9046 | 6.8231
1400 | 0.066667 | 45.5917 | 6.7522 | 46.1787 | 8.8507 | 6.7702
1401 | 0.066 | 44.7487 | 6.6894 | 45.7827 | 8.7968 | 6.7169
1402 | 0.065333 | 43.9122 | 6.6266 | 45.3853 | 8.7427 | 6.6633
1403 | 0.064667 | 43.0822 | 6.5637 | 44.9865 | 8.6885 | 6.6095
1404 | 0.064 | 42.2586 | 6.5007 | 44.5862 | 8.6341 | 6.5554
1405 | 0.063333 | 41.4417 | 6.4375 | 44.1845 | 8.5797 | 6.5009
1406 | 0.062667 | 40.6313 | 6.3743 | 43.7814 | 8.5252 | 6.4462
1407 | 0.062 | 39.8276 | 6.3109 | 43.3768 | 8.4705 | 6.3912
1408 | 0.061333 | 39.0306 | 6.2474 | 42.9708 | 8.4158 | 6.3359
1409 | 0.060667 | 38.2403 | 6.1839 | 42.5634 | 8.3609 | 6.2802
1410 | 0.06 | 37.4569 | 6.1202 | 42.1546 | 8.306 | 6.2243
1411 | 0.059333 | 36.6802 | 6.0564 | 41.7444 | 8.2509 | 6.1681
1412 | 0.058667 | 35.9104 | 5.9925 | 41.3327 | 8.1957 | 6.1116
1413 | 0.058 | 35.1475 | 5.9285 | 40.9197 | 8.1404 | 6.0548
1414 | 0.057333 | 34.3916 | 5.8644 | 40.5052 | 8.0849 | 5.9978
1415 | 0.056667 | 33.6427 | 5.8002 | 40.0893 | 8.0294 | 5.9404
1416 | 0.056 | 32.9008 | 5.7359 | 39.672 | 7.9738 | 5.8827
1417 | 0.055333 | 32.1661 | 5.6715 | 39.2533 | 7.918 | 5.8247
1418 | 0.054667 | 31.4384 | 5.607 | 38.8332 | 7.8621 | 5.7664
1419 | 0.054 | 30.7179 | 5.5424 | 38.4117 | 7.8061 | 5.7079
1420 | 0.053333 | 30.0047 | 5.4777 | 37.9888 | 7.75 | 5.649
1421 | 0.052667 | 29.2987 | 5.4128 | 37.5645 | 7.6938 | 5.5899
1422 | 0.052 | 28.6 | 5.3479 | 37.1388 | 7.6375 | 5.5304
1423 | 0.051333 | 27.9087 | 5.2829 | 36.7117 | 7.5811 | 5.4706
1424 | 0.050667 | 27.2247 | 5.2177 | 36.2833 | 7.5245 | 5.4106
1425 | 0.05 | 26.5482 | 5.1525 | 35.8534 | 7.4679 | 5.3503
1426 | 0.049333 | 25.8792 | 5.0872 | 35.4222 | 7.4111 | 5.2896
1427 | 0.048667 | 25.2177 | 5.0217 | 34.9896 | 7.3542 | 5.2287
1428 | 0.048 | 24.5638 | 4.9562 | 34.5556 | 7.2972 | 5.1674
1429 | 0.047333 | 23.9175 | 4.8905 | 34.1203 | 7.2401 | 5.1059
1430 | 0.046667 | 23.2788 | 4.8248 | 33.6836 | 7.1828 | 5.0441
1431 | 0.046 | 22.6478 | 4.759 | 33.2455 | 7.1255 | 4.982
1432 | 0.045333 | 22.0246 | 4.693 | 32.8061 | 7.068 | 4.9196
1433 | 0.044667 | 21.4091 | 4.627 | 32.3653 | 7.0104 | 4.8568
1434 | 0.044 | 20.8015 | 4.5609 | 31.9232 | 6.9527 | 4.7938
1435 | 0.043333 | 20.2017 | 4.4946 | 31.4797 | 6.8949 | 4.7305
1436 | 0.042667 | 19.6098 | 4.4283 | 31.0349 | 6.837 | 4.6669
1437 | 0.042 | 19.0259 | 4.3619 | 30.5887 | 6.7789 | 4.6031
1438 | 0.041333 | 18.45 | 4.2953 | 30.1412 | 6.7208 | 4.5389
1439 | 0.040667 | 17.8821 | 4.2287 | 29.6923 | 6.6625 | 4.4744
1440 | 0.04 | 17.3223 | 4.162 | 29.2422 | 6.6041 | 4.4096
1441 | 0.039333 | 16.7706 | 4.0952 | 28.7907 | 6.5456 | 4.3445
1442 | 0.038667 | 16.227 | 4.0283 | 28.3379 | 6.4869 | 4.2792
1443 | 0.038 | 15.6917 | 3.9613 | 27.8837 | 6.4282 | 4.2135
1444 | 0.037333 | 15.1646 | 3.8942 | 27.4283 | 6.3693 | 4.1476
1445 | 0.036667 | 14.6458 | 3.827 | 26.9715 | 6.3103 | 4.0813
1446 | 0.036 | 14.1353 | 3.7597 | 26.5135 | 6.2512 | 4.0148
1447 | 0.035333 | 13.6332 | 3.6923 | 26.0541 | 6.192 | 3.948
1448 | 0.034667 | 13.1394 | 3.6248 | 25.5935 | 6.1327 | 3.8808
1449 | 0.034 | 12.6542 | 3.5573 | 25.1316 | 6.0732 | 3.8134
1450 | 0.033333 | 12.1774 | 3.4896 | 24.6683 | 6.0136 | 3.7457
1451 | 0.032667 | 11.7091 | 3.4219 | 24.2039 | 5.9539 | 3.6777
1452 | 0.032 | 11.2494 | 3.354 | 23.7381 | 5.8941 | 3.6094
1453 | 0.031333 | 10.7983 | 3.2861 | 23.271 | 5.8342 | 3.5409
1454 | 0.030667 | 10.3559 | 3.2181 | 22.8027 | 5.7741 | 3.472
1455 | 0.03 | 9.9222 | 3.1499 | 22.3332 | 5.7139 | 3.4028
1456 | 0.029333 | 9.4972 | 3.0817 | 21.8624 | 5.6536 | 3.3334
1457 | 0.028667 | 9.0809 | 3.0135 | 21.3903 | 5.5932 | 3.2637
1458 | 0.028 | 8.6735 | 2.9451 | 20.917 | 5.5327 | 3.1936
1459 | 0.027333 | 8.2749 | 2.8766 | 20.4425 | 5.472 | 3.1233
1460 | 0.026667 | 7.8851 | 2.808 | 19.9667 | 5.4112 | 3.0527
1461 | 0.026 | 7.5043 | 2.7394 | 19.4897 | 5.3503 | 2.9818
1462 | 0.025333 | 7.1325 | 2.6707 | 19.0115 | 5.2893 | 2.9107
1463 | 0.024667 | 6.7697 | 2.6019 | 18.532 | 5.2282 | 2.8392
1464 | 0.024 | 6.4159 | 2.533 | 18.0514 | 5.1669 | 2.7675
1465 | 0.023333 | 6.0712 | 2.464 | 17.5696 | 5.1055 | 2.6954
1466 | 0.022667 | 5.7356 | 2.3949 | 17.0865 | 5.044 | 2.6231
1467 | 0.022 | 5.4091 | 2.3257 | 16.6023 | 4.9824 | 2.5505
1468 | 0.021333 | 5.0918 | 2.2565 | 16.1169 | 4.9206 | 2.4776
1469 | 0.020667 | 4.7838 | 2.1872 | 15.6303 | 4.8587 | 2.4045
1470 | 0.02 | 4.485 | 2.1178 | 15.1425 | 4.7967 | 2.331
1471 | 0.019333 | 4.1955 | 2.0483 | 14.6536 | 4.7346 | 2.2573
1472 | 0.018667 | 3.9154 | 1.9787 | 14.1635 | 4.6723 | 2.1833
1473 | 0.018 | 3.6446 | 1.9091 | 13.6723 | 4.61 | 2.109
1474 | 0.017333 | 3.3832 | 1.8394 | 13.1799 | 4.5475 | 2.0344
1475 | 0.016667 | 3.1313 | 1.7695 | 12.6864 | 4.4849 | 1.9596
1476 | 0.016 | 2.8888 | 1.6997 | 12.1917 | 4.4221 | 1.8844
1477 | 0.015333 | 2.6559 | 1.6297 | 11.696 | 4.3592 | 1.809
1478 | 0.014667 | 2.4325 | 1.5596 | 11.1991 | 4.2962 | 1.7333
1479 | 0.014 | 2.2187 | 1.4895 | 10.7011 | 4.2331 | 1.6574
1480 | 0.013333 | 2.0145 | 1.4193 | 10.202 | 4.1699 | 1.5812
1481 | 0.012667 | 1.8199 | 1.349 | 9.7018 | 4.1065 | 1.5046
1482 | 0.012 | 1.635 | 1.2787 | 9.2005 | 4.043 | 1.4279
1483 | 0.011333 | 1.4599 | 1.2083 | 8.6981 | 3.9794 | 1.3508
1484 | 0.010667 | 1.2945 | 1.1378 | 8.1947 | 3.9156 | 1.2735
1485 | 0.01 | 1.1389 | 1.0672 | 7.6902 | 3.8518 | 1.1959
1486 | 0.0093333 | 0.99306 | 0.99652 | 7.1846 | 3.7878 | 1.118
1487 | 0.0086667 | 0.8571 | 0.9258 | 6.678 | 3.7236 | 1.0399
1488 | 0.008 | 0.73103 | 0.855 | 6.1703 | 3.6594 | 0.96148
1489 | 0.0073333 | 0.61486 | 0.78413 | 5.6616 | 3.595 | 0.88281
1490 | 0.0066667 | 0.50864 | 0.71319 | 5.1519 | 3.5305 | 0.80387
1491 | 0.006 | 0.4124 | 0.64218 | 4.6412 | 3.4658 | 0.72466
1492 | 0.0053333 | 0.32615 | 0.5711 | 4.1294 | 3.4011 | 0.64519
1493 | 0.0046667 | 0.24995 | 0.49995 | 3.6167 | 3.3362 | 0.56545
1494 | 0.004 | 0.18381 | 0.42873 | 3.1029 | 3.2712 | 0.48546
1495 | 0.0033333 | 0.12776 | 0.35744 | 2.5882 | 3.206 | 0.4052
1496 | 0.0026667 | 0.081845 | 0.28609 | 2.0725 | 3.1407 | 0.32468
1497 | 0.002 | 0.04608 | 0.21466 | 1.5558 | 3.0753 | 0.24389
1498 | 0.0013333 | 0.020499 | 0.14317 | 1.0381 | 3.0098 | 0.16285
1499 | 0.00066667 | 0.0051294 | 0.07162 | 0.51954 | 2.9441 | 0.081555
1500 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## New_Parameters
a) Finding Sator Resistance and x |  | a) Finding Rotor Resistance |  | b) Finding Currents
Resistivity (ρ) (Ω.mm) | 1.72e-08 | Rotor bars (Q2) | 28 | Rotor bar current (ib) (A-rms) | 272.8629
Parallel paths (a) | 1 | Slot pitch angle (elec-deg) | 20 | End ring current (ier) (A-rms) | 607.9848
Turns per phase (Nph) | 264 | Coil span (elec-deg) | 140
Mean length of a turn (MLT) (mm) | 522.8702 | kp | 0.93969
Area of copper (mm2) | 0.99549 | kd | 0.9598
Wire diameter (mm) | 0.65 | kws | 0.90191 | c) Finding Current Densities
Stator resistance (R1) (Ω) | 2.385 | Dm (mm) | 101.5 | Current density at stator wdgs (A/mm2) | 7.6721
Layers | 2 | End ring inner diameter (di) (mm) | 80 | Current density at rotor bars (A/mm2) | 4.0424
Conductors per slot per layer | 22 | End ring width (h) (mm) | 18 | Current density at end rings (A/mm2) | 1.571
q | 3 | c (mm) | 18
Stator slots (Q1) | 36 | e (mm) | 21.5
Stator phases (m1) | 3 | Area of end ring (Aer) (mm2) | 387
Lc (mm) | 125 | Area of bar (mm2) | 67.5 | DESIGN PARAMETERS
Coil arc length (mm) | 75.564 | Length of bar (mm) | 203.8711
Coil pitch | 7 | Rb (Ω) | 5.1949e-05 | Js
Pole pitch | 9 | Rber (Ω) | 0.00012231 | Jr
Stator airgap diameter (Dg) (mm) | 123.7 | R'2 (Ω) | 2.9718 | B mag load
End ring outer diameter (Do) (mm) | 123 |  |  | G out coef
Airgap length (mm) | 0.35 |  |  | Bts
x | 30.4355 |  |  | Btr
Bbcs
Bbcr
flux per pole

## Comparison
| Calculated from test data | Computed | catalog data
G
B mag load
starting T